## Intro
United Energy (UE) 2025 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the United Energy 2025 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with United Energy. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However United Energy invites interested parties to submit their proposals or to engage in joint planning with United Energy as early as possible in order to defer or avoid the proposed augmentation. United Energy also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. In 2018, United Energy changed the format of the data for the limitations to a commonly developed Energy Networks Australia (ENA) template. This template combines the requirements of the online Australian Renewable Energy Mapping Infrastructure (AREMI) Network Opportunity Maps (NOM) and the Australian Energy Regulator (AER) template requirements in a single, consistent format that is machine readable for very large datasets. This change was made to make the format consistent across the Distribution Businesses. Note that some additional non-critical data fields that are potential additional only applicable to the NOM may be omitted. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## United Energy Limitations
Owner | Asset Code | Asset Name | Project Name | Network Element | Voltage level (kV) | Rating | [5 empty] | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Expected Energy at Risk (MWh)
[6 empty] | Summer |  |  | Winter |  |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2) |  |  |  |  | Forecast Maximum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2)
[6 empty] | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
United Energy | LMP(STO,DMA,RBD) | HGS-RBD | HGS-RBD new 66kV line | STL | 66 | 123 | 123 | - | - | - | - | - | - | - | - | - | 51975 | 92.18% | capacity | United Energy’s preferred network option is to construct a new 66kV sub-transmission line in the LMP area. See the DAPR report for more details. | 37998905 | 30% | 30% | 379989.05 | 2030/31 | 1620034.2796 | 14.9139 | 14.9149 | 10 | - | 0 | 0.99993 | 144.1013 | 146.565 | 148.1625 | 149.22 | 149.5462 | 21.1013 | 23.565 | 25.1625 | 26.22 | 26.5462 | - | - | - | - | - | 128.09 | 130.28 | 131.7 | 132.64 | 132.93 | 5.09 | 7.28 | 8.7 | 9.64 | 9.93 | - | - | - | - | - | 27.3073 | 32.3354 | 35.993 | 37.2139 | 39.7239
United Energy | DVY24 | Dandenong Valley Feeder 24 | DVY24 feeder | feeder | 22 | 11.62 | 11.62 | - | 13.53 | 13.53 | - | - | 145.1984 | -38.069 | 145.1984 | -38.069 | 171 | 34.76% | capacity | United Energy’s preferred network option is to establish a new feeder from DVY zone substation. See the DAPR report for more details. | 1288894 | 30% | 30% | 12888.94 | 2026/27 | 54950.3325 | 3.7085 | 3.7208 | 0 | 0 | 0 | 0.9967 | 13.7385 | 16.3123 | 17.301 | 17.3505 | 17.2966 | 2.1185 | 4.6923 | 5.681 | 5.7305 | 5.6766 | - | - | - | - | - | 12.3286 | 14.9245 | 15.956 | 16.0207 | 15.985 | 0.70861 | 3.3045 | 4.336 | 4.4007 | 4.365 | - | - | - | - | - | 4.2 | 4.5 | 4.8 | 5.1 | 5.4
United Energy | EW | Elwood No.2 Transformer | Elwood No.2 Transformer Replacement | zss | 66/11 | 58.8 | 29.4 | 0 | 58.8 | 29.4 | 0 | 30 | 144.9886 | -37.8823 | 144.9886 | -37.8823 | 14890 | 93.51% | asset condition | United Energy’s preferred network option is to replace the #2 transformer at EW. See the DAPR report for more details. | 4621926.2206 | 30% | 30% | 46219.2622 | 2028 | 197049.8601 | 4.1 | 4.1074 | 0 | 0 | 2.99 | 0.9982 | 28.51 | 29.2 | 29.77 | 30.14 | 30.44 | 0 | 0 | 0 | 0 | 0 | 25.52 | 26.21 | 26.78 | 27.15 | 27.45 | 24.94 | 25.52 | 25.99 | 26.29 | 26.52 | 0 | 0 | 0 | 0 | 0 | 21.95 | 22.53 | 23 | 23.3 | 23.53 | 2.8844 | 3.0746 | 3.2546 | 3.4089 | 3.5558
United Energy | EW | Elwood Switchboard and Relay | Elwood Switchboard and Relay Replacement | zss | 66/11 | 58.8 | 29.4 | 0 | 58.8 | 29.4 | 0 | N/A | 144.9886 | -37.8823 | 144.9886 | -37.8823 | 14890 | 93.51% | asset condition | United Energy’s preferred network option is to replace the 11kV switchboard and relay at EW. See the DAPR report for more details. | 5691482.7468 | 30% | 30% | 56914.8275 | 2027 | 242649.0224 | 5 | 5.009 | 0 | 0 | 2.99 | 0.9982 | 28.51 | 29.2 | 29.77 | 30.14 | 30.44 | 0 | 0 | 0 | 0 | 0 | 25.52 | 26.21 | 26.78 | 27.15 | 27.45 | 24.94 | 25.52 | 25.99 | 26.29 | 26.52 | 0 | 0 | 0 | 0 | 0 | 21.95 | 22.53 | 23 | 23.3 | 23.53 | 6.9529 | 7.1942 | 7.3961 | 7.5274 | 7.633

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
BT-NB | S | 94.8 | 0.94076 | 22.8631 | - | - | 84.4 | 85.6 | 86.8 | 87.9 | 87.9 | 88.4 | - | - | - | - | - | - | - | - | - | - | - | -
BT-NB | W | 101.7 | 0.99171 | 22.8631 | - | - | 60.3 | 65.7 | 68.4 | 71.4 | 74.2 | 77.2 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-OE | S | 65.2 | 0.979 | 5.2224 | - | - | 38.1 | 41.6 | 44.1 | 46.5 | 46.5 | 46.5 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-OE | W | 91.5 | 0.98452 | 5.2224 | - | - | 32.3 | 37.8 | 41.4 | 43.4 | 44.5 | 45.5 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN | S | 118.3 | 0.93594 | 36.5567 | - | - | 92.1 | 94.8 | 97.3 | 101 | 101.9 | 100.3 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN | W | 130.3 | 0.95318 | 36.5567 | - | - | 89.7 | 102.3 | 106.3 | 109 | 110.8 | 109.8 | - | - | - | - | - | - | - | - | - | - | - | -
GW-NO | S | 94.9 | 0.99653 | 66.0868 | - | - | 57.7 | 62.4 | 64 | 64.9 | 64.8 | 64.7 | - | - | - | - | - | - | - | - | - | - | - | -
GW-NO | W | 101.7 | 0.99105 | 66.0868 | - | - | 44.7 | 47 | 48.9 | 50.6 | 52.1 | 53.5 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-MR | S | 128 | 0.93275 | 18.9022 | - | - | 138.3 | 137.9 | 139.2 | 139.4 | 139.6 | 139.5 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-MR | W | 133.7 | 0.98935 | 18.9022 | - | - | 93.9 | 102.2 | 106.1 | 111 | 115.4 | 119.7 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN/HPK | S | 117.2 | 0.92321 | 36.5567 | - | - | 59.9 | 59.8 | 60.9 | 62.4 | 62.4 | 62 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN/HPK | W | 126.3 | 0.95038 | 36.5567 | - | - | 52.4 | 59.9 | 62.5 | 63.8 | 64 | 64.5 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | S | 117.2 | 0.96154 | 0 | - | - | 62.4 | 65.3 | 65.7 | 65.5 | 65.2 | 64.8 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | W | 126.3 | 0.98058 | 0 | - | - | 61.8 | 69 | 70.1 | 72.5 | 74.7 | 76.5 | - | - | - | - | - | - | - | - | - | - | - | -
KBH-M-MC | S | 78.3 | 0.98973 | 57.4382 | - | - | 29.2 | 30.9 | 32.5 | 34.6 | 35.4 | 36.2 | - | - | - | - | - | - | - | - | - | - | - | -
KBH-M-MC | W | 78.3 | 0.98188 | 57.4382 | - | - | 27.6 | 30.7 | 33.5 | 36 | 37.4 | 38.6 | - | - | - | - | - | - | - | - | - | - | - | -
SR-CM | S | 94.9 | 1 | 14.3653 | - | - | 61.8 | 71.9 | 75.3 | 79.4 | 78.9 | 77.9 | - | - | - | - | - | - | - | - | - | - | - | -
SR-CM | W | 101.7 | 1 | 14.3653 | - | - | 56.9 | 63 | 69.8 | 73.3 | 74.5 | 74.8 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SV | S | 128 | 0.95158 | 15.2168 | - | - | 88.8 | 97.4 | 98.6 | 99.7 | 99.2 | 98.7 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SV | W | 136.6 | 0.97954 | 15.2168 | - | - | 78.2 | 92.5 | 95.5 | 96.9 | 97 | 97.8 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-BR | S | 97.2 | 0.95232 | 12.7852 | - | - | 83.9 | 83.7 | 86.1 | 87.9 | 87.8 | 87.4 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-BR | W | 97.2 | 0.95028 | 12.7852 | - | - | 70.4 | 78 | 81.1 | 83.5 | 84.9 | 86.1 | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-CRM | S | 128 | 0.97023 | 64.3961 | - | - | 114.2 | 123.9 | 125.5 | 126.9 | 126.9 | 126.5 | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-CRM | W | 133.7 | 0.97643 | 64.3961 | - | - | 97.6 | 102.4 | 105.4 | 109 | 112.3 | 115.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | S | 90.3 | 0.96148 | 12.4823 | - | - | 62.3 | 66 | 66.4 | 66.2 | 66 | 65.5 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | W | 104.6 | 0.98706 | 12.4823 | - | - | 61.8 | 68.4 | 69.6 | 71.8 | 74.1 | 75.9 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SS | S | 108.6 | 0.98567 | 30.1479 | - | - | 90.7 | 87.9 | 88.7 | 90.4 | 90.8 | 90.9 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SS | W | 115.5 | 0.99744 | 30.1479 | - | - | 78.2 | 73.8 | 77.5 | 80.3 | 82 | 84.5 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW1 | S | 12.8 | 0.9845 | 12.6848 | - | - | 12.9 | 12.6 | 12.9 | 13 | 13.1 | 13.2 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW1 | W | 14.9 | 1 | 12.6848 | - | - | 9.2 | 10.2 | 10.6 | 11.3 | 11.9 | 12.6 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | S | 85.7 | 0.91185 | 4.6943 | - | - | 32.9 | 33.7 | 33.9 | 34 | 34.1 | 34.2 | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | W | 101.7 | 0.92464 | 4.6943 | - | - | 34.5 | 35.7 | 36.2 | 36.6 | 37.1 | 37.8 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M2 | S | 72.6 | 0.9809 | 15.1827 | - | - | 73.3 | 73.1 | 75.8 | 77.7 | 78.5 | 78.2 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M2 | W | 72.6 | 0.9835 | 15.1827 | - | - | 60.6 | 65.7 | 69.2 | 71.6 | 73.2 | 74.7 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS2 | S | 88.6 | 0.96667 | 31.1751 | - | - | 42 | 54.1 | 54.4 | 54.5 | 54.6 | 54.5 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS2 | W | 88.6 | 0.9797 | 31.1751 | - | - | 39.4 | 44 | 44.6 | 46.2 | 47.4 | 48.1 | - | - | - | - | - | - | - | - | - | - | - | -
CM-HT | S | 97.2 | 0.99012 | 18.953 | - | - | 50.6 | 86.7 | 87.7 | 88.1 | 88.3 | 88.4 | - | - | - | - | - | - | - | - | - | - | - | -
CM-HT | W | 109.2 | 1 | 18.953 | - | - | 41 | 44.8 | 50.9 | 54 | 54.9 | 55 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS1 | S | 88.6 | 0.96667 | 31.1751 | - | - | 42 | 54.1 | 54.4 | 54 | 54.6 | 54.5 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS1 | W | 88.6 | 0.9797 | 31.1751 | - | - | 39.4 | 44 | 44.6 | 46.2 | 47.4 | 48.1 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-CDA | S | 65.2 | 0.97644 | 9.2696 | - | - | 38.2 | 41.8 | 44.3 | 46.7 | 46.7 | 46.6 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-CDA | W | 91.5 | 0.98148 | 9.2696 | - | - | 32.4 | 37.7 | 41.6 | 43.5 | 44.6 | 45.7 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-CFD | S | 94.9 | 0.94615 | 11.9088 | - | - | 91 | 94.8 | 96.1 | 97.3 | 97.9 | 97.8 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-CFD | W | 98.9 | 0.9795 | 11.9088 | - | - | 63.4 | 67.7 | 70.1 | 73.3 | 75.8 | 78.1 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M | S | 97.2 | 0.97584 | 15.1827 | - | - | 74.5 | 74.2 | 76.9 | 79.2 | 79.6 | 79.6 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M | W | 97.2 | 0.97727 | 15.1827 | - | - | 61.6 | 66.3 | 69.7 | 72.6 | 74.4 | 75.8 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-NB | S | 128 | 0.90764 | 12.93 | 11.2732 | 3 | 144 | 143 | 145 | 146.8 | 146.5 | 146.8 | 11.72% | 15 | 327.0429 | 316.6916 | 390.9794 | 423.0372 | 938.6724 | 17.1772 | 15.03 | 18.7875 | 19.3243 | 34.3544
HTS-NB | W | 133.7 | 0.98023 | 12.93 | - | - | 96.1 | 104.9 | 109.8 | 114.6 | 119.1 | 124.4 | - | - | - | - | - | - | - | - | - | - | - | -
EB-RD | S | 65.2 | 0.98545 | 24.9684 | - | - | 55 | 54.3 | 55 | 55.3 | 55.3 | 55.3 | - | - | - | - | - | - | - | - | - | - | - | -
EB-RD | W | 77.2 | 0.99765 | 24.9684 | - | - | 42.6 | 44.9 | 46.6 | 48.9 | 51 | 53 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NO | S | 128 | 0.99559 | 35.6278 | - | - | 90.8 | 97.6 | 100 | 101.5 | 101.3 | 101.1 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NO | W | 133.7 | 0.99077 | 35.6278 | - | - | 75.8 | 81.5 | 84.5 | 86.9 | 88.7 | 90.5 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-FTS | S | 94 | 0.98289 | 0 | - | - | 76 | 84.4 | 85.5 | 86.9 | 87.4 | 87.3 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-FTS | W | 96 | 0.99034 | 0 | - | - | 62.1 | 65.6 | 67.2 | 70.2 | 71.8 | 74 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM/EL | S | 100.6 | 0.97513 | 21.9131 | - | - | 76.4 | 80.5 | 81 | 82 | 82.2 | 82.2 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM/EL | W | 108.6 | 0.98046 | 21.9131 | - | - | 56.3 | 60.1 | 62.4 | 64.9 | 67.4 | 69.6 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-BU | S | 100.6 | 0.95141 | 11.4779 | - | - | 88.5 | 90 | 91.3 | 92.1 | 93 | 92.8 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-BU | W | 112 | 0.99307 | 11.4779 | - | - | 57.7 | 63 | 64.9 | 67.2 | 69.5 | 72.2 | - | - | - | - | - | - | - | - | - | - | - | -
OE-CDA | S | 84 | 0.98367 | 14.492 | - | - | 24.5 | 27.2 | 28.7 | 30 | 30 | 30 | - | - | - | - | - | - | - | - | - | - | - | -
OE-CDA | W | 101.7 | 0.98522 | 14.492 | - | - | 20.3 | 23.9 | 26 | 27.2 | 28 | 28.8 | - | - | - | - | - | - | - | - | - | - | - | -
FTS-LWN | S | 128 | 0.96975 | 25.5749 | - | - | 112.4 | 120.9 | 123.6 | 123.8 | 123.9 | 123.7 | - | - | - | - | - | - | - | - | - | - | - | -
FTS-LWN | W | 133.7 | 0.97989 | 25.5749 | - | - | 94.5 | 98 | 102 | 106 | 108.8 | 111.9 | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FSH | S | 84 | 0.9959 | 40.9888 | - | - | 73.1 | 80.3 | 81.3 | 82.5 | 82.9 | 82.8 | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FSH | W | 96 | 0.99834 | 40.9888 | - | - | 60.4 | 63.5 | 65 | 67.7 | 69.1 | 71.1 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM | S | 100.6 | 0.98273 | 14.1147 | - | - | 69.5 | 72.2 | 73.6 | 74.4 | 74.5 | 74.5 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM | W | 108.6 | 0.99022 | 14.1147 | - | - | 51.1 | 54.5 | 56.5 | 58.7 | 60.7 | 62.6 | - | - | - | - | - | - | - | - | - | - | - | -
DN-DSH-DVY | S | 128 | 0.9589 | 82.4862 | - | - | 58.4 | 65.2 | 66.7 | 69 | 70 | 69.5 | - | - | - | - | - | - | - | - | - | - | - | -
DN-DSH-DVY | W | 136.6 | 0.96593 | 82.4862 | - | - | 58.7 | 67.4 | 68.3 | 70.1 | 71.4 | 70.1 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-LD | S | 128 | 0.97195 | 34.2166 | - | - | 121.2 | 123.9 | 126.4 | 128.1 | 128.3 | 127.4 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-LD | W | 133.7 | 0.99381 | 34.2166 | - | - | 96.9 | 101.5 | 105.7 | 109.9 | 114.5 | 115.5 | - | - | - | - | - | - | - | - | - | - | - | -
SS-NP | S | 84 | 0.97645 | 59.0211 | - | - | 55.2 | 54.8 | 54.9 | 55.4 | 55.8 | 55.9 | - | - | - | - | - | - | - | - | - | - | - | -
SS-NP | W | 96.6 | 0.99374 | 59.0211 | - | - | 47.9 | 49 | 50.9 | 52.7 | 54 | 55.8 | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO2 | S | 56 | 0.99751 | 51.2696 | - | - | 40.1 | 46 | 46.9 | 48.2 | 47.9 | 48.5 | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO2 | W | 60 | 1 | 51.2696 | - | - | 19.9 | 20.5 | 21.1 | 22.1 | 22.8 | 23.2 | - | - | - | - | - | - | - | - | - | - | - | -
LD-MGE | S | 80 | 0.97691 | 72.6125 | - | - | 69.3 | 73.5 | 74 | 74.5 | 74.7 | 73.8 | - | - | - | - | - | - | - | - | - | - | - | -
LD-MGE | W | 88.6 | 0.99642 | 72.6125 | - | - | 55.8 | 59.9 | 62.1 | 63.7 | 66.2 | 66.4 | - | - | - | - | - | - | - | - | - | - | - | -
MTN-DMA | S | 128 | 0.99087 | 65.957 | 25.2221 | 1.0625 | 120.5 | 142.7 | 145.3 | 147 | 147.7 | 148.2 | 11.48% | 14.7 | 0.88125 | 1.7882 | 2.5141 | 3.0688 | 3.2599 | 0.375 | 0.5 | 0.5625 | 0.625 | 0.6875
MTN-DMA | W | 134 | 0.9974 | 65.957 | - | - | 76.8 | 80 | 82.7 | 85.7 | 88.5 | 91.3 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW3 | S | 12.8 | 0.97656 | 12.6848 | - | - | 12.8 | 12.4 | 12.7 | 12.8 | 12.9 | 13 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW3 | W | 15.6 | 1 | 12.6848 | - | - | 9.1 | 10 | 10.4 | 11.1 | 11.7 | 12.4 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-GW | S | 128 | 0.99779 | 30.4591 | - | - | 90.4 | 97.3 | 99.1 | 100.5 | 100.4 | 100.1 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-GW | W | 131.5 | 0.99339 | 30.4591 | - | - | 75.7 | 81.4 | 84.3 | 86.8 | 88.5 | 89.8 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OR | S | 81.7 | 0.9881 | 13.5068 | - | - | 75.6 | 72.6 | 74.4 | 76.8 | 78.4 | 78.6 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OR | W | 89.2 | 1 | 13.5068 | - | - | 50.1 | 54.6 | 58 | 62.6 | 66.2 | 69.4 | - | - | - | - | - | - | - | - | - | - | - | -
DMA-RBD1 | S | 68.6 | 0.99873 | 50.4483 | 11.9163 | 1.0625 | 79 | 90.6 | 92.3 | 93.3 | 93.5 | 93.6 | 32.07% | 22 | 0.88125 | 1.7882 | 2.5141 | 3.0688 | 3.2599 | 0.375 | 0.5 | 0.5625 | 0.625 | 0.6875
DMA-RBD1 | W | 68.6 | 0.99797 | 50.4483 | - | - | 49.3 | 50.7 | 52.4 | 54 | 55.5 | 57.2 | - | - | - | - | - | - | - | - | - | - | - | -
DMA-RBD2 | S | 70 | 1 | 50.4483 | 11.9163 | 1.0625 | 78.9 | 90.6 | 92.2 | 93.3 | 93.5 | 93.6 | 29.43% | 20.6 | 0.88125 | 1.7882 | 2.5141 | 3.0688 | 3.2599 | 0.375 | 0.5 | 0.5625 | 0.625 | 0.6875
DMA-RBD2 | W | 75 | 0.99797 | 50.4483 | - | - | 49.3 | 50.7 | 52.4 | 54 | 55.5 | 57.2 | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FTN | S | 76.6 | 0.98736 | 22.2942 | - | - | 71.2 | 77.2 | 78.3 | 79 | 79.1 | 78.9 | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FTN | W | 94.3 | 0.99491 | 22.2942 | - | - | 58.9 | 62 | 63.9 | 66 | 68 | 69.8 | - | - | - | - | - | - | - | - | - | - | - | -
BU-WD | S | 100 | 0.95717 | 19.6529 | - | - | 53.7 | 57.1 | 58.1 | 58.5 | 59.1 | 59.2 | - | - | - | - | - | - | - | - | - | - | - | -
BU-WD | W | 117.7 | 0.99443 | 19.6529 | - | - | 35.9 | 39.3 | 40.3 | 41.5 | 42.7 | 44.3 | - | - | - | - | - | - | - | - | - | - | - | -
EW-SK | S | 86.3 | 0.99465 | 4.6943 | - | - | 18.7 | 19.9 | 20.3 | 20.7 | 20.9 | 21.1 | - | - | - | - | - | - | - | - | - | - | - | -
EW-SK | W | 91.5 | 0.99543 | 4.6943 | - | - | 21.9 | 24.6 | 25.6 | 26.4 | 27.3 | 28 | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-NW | S | 128 | 0.96901 | 28.1572 | - | - | 106.5 | 115.5 | 118.4 | 121.3 | 122.5 | 123.1 | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-NW | W | 130.3 | 0.98507 | 28.1572 | - | - | 87.1 | 105.7 | 110.3 | 116.1 | 121.3 | 126.1 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-WD | S | 93.2 | 0.94183 | 8.175 | - | - | 89.4 | 90.2 | 92 | 92.8 | 93.1 | 93.2 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-WD | W | 104.6 | 0.98967 | 8.175 | - | - | 58.1 | 63.1 | 65 | 68.1 | 70.4 | 72.7 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OAK | S | 94.9 | 0.98287 | 13.094 | - | - | 75.9 | 73.5 | 74.7 | 77.5 | 79.1 | 79.3 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OAK | W | 98.9 | 0.99801 | 13.094 | - | - | 50.2 | 54.3 | 58.3 | 62.9 | 66.9 | 70.2 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-HPK | S | 102.3 | 0.82192 | 0 | - | - | 58.4 | 54.4 | 54.2 | 53.6 | 54 | 53.8 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-HPK | W | 126.3 | 0.94459 | 0 | - | - | 37.9 | 43.7 | 45.5 | 46.3 | 46.5 | 46.9 | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | S | 91.5 | 0.95714 | 12.4823 | - | - | 49 | 52 | 52.3 | 52.1 | 51.8 | 51.5 | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | W | 105.7 | 0.98834 | 12.4823 | - | - | 34.3 | 37.7 | 38.4 | 39.8 | 41.4 | 42.2 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-HT | S | 128 | 0.99787 | 15.7623 | - | - | 94.1 | 135.5 | 140.2 | 144.6 | 144.3 | 143.6 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-HT | W | 133.7 | 1 | 15.7623 | - | - | 77.8 | 84.8 | 92.1 | 96 | 98.1 | 100.5 | - | - | - | - | - | - | - | - | - | - | - | -
BR-MC | S | 90.3 | 0.96038 | 35.7202 | - | - | 53 | 53.6 | 55.5 | 57 | 56.9 | 56.5 | - | - | - | - | - | - | - | - | - | - | - | -
BR-MC | W | 90.3 | 0.93933 | 35.7202 | - | - | 51.1 | 57.1 | 59.4 | 60.8 | 61.3 | 61.6 | - | - | - | - | - | - | - | - | - | - | - | -
CFD-EL | S | 94.9 | 0.97688 | 19.7072 | - | - | 51.9 | 52.6 | 53.6 | 53.9 | 53.9 | 54 | - | - | - | - | - | - | - | - | - | - | - | -
CFD-EL | W | 98.9 | 0.99237 | 19.7072 | - | - | 39.3 | 41.3 | 42.6 | 43.8 | 45.1 | 46.4 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC2 | S | 100.6 | 0.94545 | 33.7818 | - | - | 88 | 85.3 | 87 | 89.3 | 89.7 | 91.1 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC2 | W | 108.6 | 0.99502 | 33.7818 | - | - | 60.2 | 66 | 70.2 | 74.2 | 78.9 | 83.1 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH/BW | S | 17.5 | 0.9863 | 15.2253 | - | - | 7.3 | 7.3 | 7.4 | 7.5 | 7.6 | 7.6 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH/BW | W | 19.1 | 1 | 15.2253 | - | - | 5.3 | 5.8 | 6.1 | 6.5 | 6.9 | 7.3 | - | - | - | - | - | - | - | - | - | - | - | -
OAK-OR | S | 84 | 0.99746 | 26.6007 | - | - | 39.3 | 37.5 | 38 | 39.4 | 40.7 | 40.8 | - | - | - | - | - | - | - | - | - | - | - | -
OAK-OR | W | 98.9 | 0.99275 | 26.6007 | - | - | 27.6 | 29 | 31.2 | 33 | 35.1 | 36.9 | - | - | - | - | - | - | - | - | - | - | - | -
MR-BT | S | 75.4 | 0.94055 | 28.8353 | - | - | 84.1 | 81.7 | 82.6 | 83.2 | 83.4 | 83.3 | - | - | - | - | - | - | - | - | - | - | - | -
MR-BT | W | 81.1 | 0.98976 | 28.8353 | - | - | 58.6 | 62.4 | 64.9 | 67.7 | 70.2 | 72.7 | - | - | - | - | - | - | - | - | - | - | - | -
FSH-MTN | S | 77 | 0.99342 | 80.2687 | - | - | 60.8 | 64 | 64.6 | 65.9 | 65.6 | 66.1 | - | - | - | - | - | - | - | - | - | - | - | -
FSH-MTN | W | 96 | 0.99302 | 80.2687 | - | - | 57.3 | 60.3 | 62.4 | 64.3 | 66.1 | 68.2 | - | - | - | - | - | - | - | - | - | - | - | -
BH-NW | S | 102 | 0.97942 | 39.2309 | - | - | 58.3 | 58.6 | 59.2 | 59.7 | 60.9 | 61.4 | - | - | - | - | - | - | - | - | - | - | - | -
BH-NW | W | 115 | 0.99569 | 39.2309 | - | - | 46.4 | 54.6 | 57 | 59.7 | 61.6 | 63.4 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SVW | S | 128 | 0.95158 | 29.6561 | - | - | 88.8 | 97.4 | 99 | 100 | 99.6 | 99 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SVW | W | 136.6 | 0.97834 | 29.6561 | - | - | 78.5 | 93.1 | 94.9 | 96.3 | 97.3 | 97.8 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH3 | S | 14.3 | 0.98649 | 2.5405 | - | - | 7.4 | 7.3 | 7.5 | 7.6 | 7.6 | 7.7 | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH3 | W | 15.2 | 1 | 2.5405 | - | - | 5.3 | 5.8 | 6.1 | 6.5 | 6.9 | 7.3 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DSH | S | 128 | 0.93688 | 11.7446 | - | - | 80.8 | 86.5 | 90 | 95 | 95.6 | 94.6 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DSH | W | 133.7 | 0.95125 | 11.7446 | - | - | 80 | 90.8 | 96.9 | 99.9 | 100.3 | 100.2 | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-FTS2 | S | 94.3 | 0.93782 | 0 | 35.982 | 2 | 98.1 | 107.6 | 110.3 | 110.5 | 110.6 | 110.3 | 14.1% | 13.3 | - | - | - | - | - | - | - | - | - | -
CBTS-FTS2 | W | 123.5 | 0.95737 | 0 | - | - | 82.1 | 85.2 | 89.2 | 93 | 95.9 | 98.9 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-SR | S | 128 | 0.99262 | 11.1746 | - | - | 94.8 | 139.4 | 143.8 | 148.7 | 148.5 | 147.6 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-SR | W | 133.7 | 0.99745 | 11.1746 | - | - | 78.5 | 86.8 | 94.5 | 99.1 | 101.2 | 102.4 | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-BH | S | 120 | 0.95404 | 11.0737 | - | - | 108.8 | 119.3 | 121.6 | 123.9 | 126.9 | 127.4 | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-BH | W | 132.6 | 0.97836 | 11.0737 | - | - | 87.8 | 107.8 | 112.5 | 118.5 | 124.2 | 129.4 | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-FTS1 | S | 94.3 | 0.93841 | 0 | 35.982 | 2 | 95.8 | 105.1 | 107.7 | 108 | 108.1 | 107.7 | 11.45% | 10.8 | - | - | - | - | - | - | - | - | - | -
CBTS-FTS1 | W | 123.5 | 0.95761 | 0 | - | - | 80.2 | 83.3 | 87.2 | 90.9 | 93.6 | 96.6 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NP | S | 108.6 | 0.98355 | 28.8732 | - | - | 91.2 | 87.9 | 89.6 | 91.3 | 91.7 | 91.8 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NP | W | 115.5 | 0.99618 | 28.8732 | - | - | 78.6 | 74.3 | 77.5 | 80.3 | 82.5 | 84.5 | - | - | - | - | - | - | - | - | - | - | - | -
CRM-FTN/LWN | S | 76 | 0.99209 | 112.2651 | - | - | 75.9 | 81.5 | 83.6 | 82.8 | 82.8 | 82.5 | - | - | - | - | - | - | - | - | - | - | - | -
CRM-FTN/LWN | W | 96.5 | 0.98264 | 112.2651 | - | - | 74.9 | 75.7 | 78.7 | 81.1 | 83.2 | 85.1 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN1 | S | 109 | 0.97026 | 39.2799 | - | - | 97.5 | 111.7 | 113.5 | 115 | 115.7 | 115.7 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN1 | W | 116 | 0.99068 | 39.2799 | - | - | 75.1 | 79.1 | 81.4 | 84.6 | 87.1 | 89.2 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-KBH | S | 87.5 | 0.96707 | 19.3205 | - | - | 33.4 | 34.5 | 35.8 | 37.4 | 38 | 38.3 | - | - | - | - | - | - | - | - | - | - | - | -
HTS-KBH | W | 87.5 | 0.96599 | 19.3205 | - | - | 29.4 | 32.6 | 34.7 | 36.7 | 38.1 | 39.4 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN2 | S | 128 | 0.97424 | 39.2799 | - | - | 89.3 | 100 | 101.6 | 103.3 | 103.8 | 103.7 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN2 | W | 134 | 0.98707 | 39.2799 | - | - | 69.6 | 73.4 | 75.3 | 78.5 | 80.4 | 82.7 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC1 | S | 93.2 | 0.94761 | 33.7818 | - | - | 87.8 | 85.2 | 86.8 | 88.2 | 89.6 | 90 | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC1 | W | 104.6 | 0.99501 | 33.7818 | - | - | 60.1 | 65.3 | 69.4 | 74.1 | 78 | 82.9 | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-DMA | S | 128 | 0.96934 | 26.6771 | 8.7204 | 1.0625 | 127.2 | 156.5 | 159.1 | 161.3 | 162.8 | 163.9 | 22.27% | 28.5 | 0.88125 | 1.7882 | 2.5141 | 3.0688 | 3.2599 | 0.375 | 0.5 | 0.5625 | 0.625 | 0.6875
TBTS-DMA | W | 134 | 0.99112 | 26.6771 | - | - | 78.8 | 82.6 | 85.1 | 88.6 | 91.6 | 94.6 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DVY | S | 128 | 0.92382 | 34.1848 | - | - | 82.7 | 89.4 | 96.8 | 105.7 | 105.9 | 105 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DVY | W | 133.7 | 0.93571 | 34.1848 | - | - | 84 | 95 | 105.4 | 109.7 | 109.4 | 110.8 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-MGE | S | 128 | 0.97366 | 38.3959 | - | - | 121.5 | 123.5 | 126.3 | 128 | 128.7 | 127.3 | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-MGE | W | 133.7 | 0.99379 | 38.3959 | - | - | 96.6 | 101.3 | 105.4 | 109.7 | 112.7 | 115.8 | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO1 | S | 56 | 0.99751 | 51.2696 | - | - | 40.1 | 45.9 | 46.8 | 48.2 | 48.7 | 48.5 | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO1 | W | 60 | 1 | 51.2696 | - | - | 19.9 | 20.5 | 21.1 | 21.8 | 22.4 | 23.2 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | S | 94.9 | 0.97842 | 24.9684 | - | - | 55.6 | 55 | 56.3 | 56.1 | 56.7 | 56.7 | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | W | 101.7 | 0.9954 | 24.9684 | - | - | 43.5 | 45.3 | 47.6 | 49.6 | 51.5 | 53.6 | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Import Rating (MVA) | Station N-1 Import Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Maximum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Maximum Demand (Hrs) | Actual Maximum Demand (MVA) | 10% POE |  |  |  |  | 50% POE |  |  |  |  | 50% POE load above N-1 Import Rating (%) | 50% POE load above N-1 Import Rating (MVA) | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted POE
[10 empty] | Forecast Maximum Demand (MVA) |  |  |  |  | Forecast Maximum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs) |  |  |  |  | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh)
[5 empty] | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
BH | summer | 107.68 | 71.79 | 99 | 0.98201 | 11.0737 | 26.5514 | 1.9247 | 46.0962 | 58.43 | 60.02 | 61.66 | 62.9 | 63.43 | 54.24 | 55.72 | 57.32 | 58.55 | 59.06 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BH | winter | 130.83 | 87.22 | 99 | 2025: 0.99115; 2025: 11.0737; 2026: 26.5514; 2025: 1.527; 2025: 39.2367; Forecast Maximum Demand (MVA) 2026: 59.13; Forecast Maximum Demand (MVA) 2027: 61.03; Forecast Maximum Demand (MVA) 2028: 63.57; Forecast Maximum Demand (MVA) 2029: 65.19; Forecast Maximum Demand (MVA) 2030: 66.97; Forecast Maximum Demand (MVA) 2026: 52.88; Forecast Maximum Demand (MVA) 2027: 54.82; Forecast Maximum Demand (MVA) 2028: 57.28; Forecast Maximum Demand (MVA) 2029: 58.85; Forecast Maximum Demand (MVA) 2030: 60.66; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BR | summer | 61.62 | 30.81 | 60 | 0.99024 | 12.7852 | 6.7947 | 1.9624 | 29.2822 | 31.77 | 32.13 | 32.4 | 32.53 | 32.53 | 28.25 | 28.54 | 28.69 | 28.79 | 28.72 | - | - | 0 | 0.14 | 0.33 | 0.38 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042 | 0.099 | 0.114 | 0.123 | 0 | 0 | 0 | 0 | 0
BR | winter | 63.41 | 31.7 | 60 | 2025: 0.9995; 2025: 12.7852; 2026: 6.7947; 2025: 0.8732; 2025: 20.0997; Forecast Maximum Demand (MVA) 2026: 22.14; Forecast Maximum Demand (MVA) 2027: 22.82; Forecast Maximum Demand (MVA) 2028: 23.7; Forecast Maximum Demand (MVA) 2029: 24.6; Forecast Maximum Demand (MVA) 2030: 25.44; Forecast Maximum Demand (MVA) 2026: 21; Forecast Maximum Demand (MVA) 2027: 21.66; Forecast Maximum Demand (MVA) 2028: 22.53; Forecast Maximum Demand (MVA) 2029: 23.39; Forecast Maximum Demand (MVA) 2030: 24.23; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BT | summer | 61.03 | 30.51 | 60 | 0.999 | 9.9331 | 6.1304 | 2.6455 | 32.5403 | 39.52 | 40.17 | 40.66 | 40.99 | 41.22 | 32.65 | 33.19 | 33.6 | 33.96 | 34.17 | 0.070141 | 2.14 | 133.19 | 169.19 | 207.25 | 237.6 | 291.58 | 0.33 | 0.42 | 0.52 | 0.59 | 0.73 | 49.5 | 56 | 65 | 73 | 89 | 1.69 | 2.71 | 4.14 | 6.79 | 9.47 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 1.5 | 2.5 | 4 | 8.5 | 10.5 | 41.14 | 52.654 | 65.073 | 76.033 | 94.103 | 0.099 | 0.133 | 0.163 | 0.191 | 0.233
BT | winter | 63.41 | 31.7 | 60 | 2025: 0.9991; 2025: 9.9331; 2026: 6.1304; 2025: 1.4578; 2025: 25.0772; Forecast Maximum Demand (MVA) 2026: 28.41; Forecast Maximum Demand (MVA) 2027: 29.39; Forecast Maximum Demand (MVA) 2028: 30.56; Forecast Maximum Demand (MVA) 2029: 31.71; Forecast Maximum Demand (MVA) 2030: 32.83; Forecast Maximum Demand (MVA) 2026: 26.34; Forecast Maximum Demand (MVA) 2027: 27.34; Forecast Maximum Demand (MVA) 2028: 28.49; Forecast Maximum Demand (MVA) 2029: 29.66; Forecast Maximum Demand (MVA) 2030: 30.86; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BU | summer | 68.98 | 34.49 | 60 | 0.98959 | 11.4779 | 7.1401 | 2.1353 | 31.8856 | 33.09 | 33.45 | 33.71 | 33.9 | 33.82 | 30.28 | 30.6 | 30.89 | 31.08 | 31.01 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BU | winter | 70.11 | 35.05 | 60 | 2025: 0.99964; 2025: 11.4779; 2026: 7.1401; 2025: 1.3547; 2025: 21.3277; Forecast Maximum Demand (MVA) 2026: 23.95; Forecast Maximum Demand (MVA) 2027: 24.78; Forecast Maximum Demand (MVA) 2028: 25.92; Forecast Maximum Demand (MVA) 2029: 26.99; Forecast Maximum Demand (MVA) 2030: 27.98; Forecast Maximum Demand (MVA) 2026: 22.76; Forecast Maximum Demand (MVA) 2027: 23.56; Forecast Maximum Demand (MVA) 2028: 24.66; Forecast Maximum Demand (MVA) 2029: 25.63; Forecast Maximum Demand (MVA) 2030: 26.55; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
BW | summer | 37.79 | 25.2 | 40.5 | 0.99704 | 12.6848 | 3.3983 | 3.7007 | 24.053 | 25.79 | 26.2 | 26.47 | 26.67 | 26.83 | 23.51 | 23.89 | 24.13 | 24.36 | 24.5 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BW | winter | 42.27 | 28.18 | 40.5 | 2025: 0.99886; 2025: 12.6848; 2026: 3.3983; 2025: 1.2668; 2025: 17.5683; Forecast Maximum Demand (MVA) 2026: 21.31; Forecast Maximum Demand (MVA) 2027: 22.21; Forecast Maximum Demand (MVA) 2028: 23.29; Forecast Maximum Demand (MVA) 2029: 24.38; Forecast Maximum Demand (MVA) 2030: 25.47; Forecast Maximum Demand (MVA) 2026: 19.14; Forecast Maximum Demand (MVA) 2027: 20.03; Forecast Maximum Demand (MVA) 2028: 21.11; Forecast Maximum Demand (MVA) 2029: 22.25; Forecast Maximum Demand (MVA) 2030: 23.4; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CDA | summer | 59.17 | 25.69 | 53 | 0.99363 | 9.2696 | 11.1541 | 1.6611 | 24.3565 | 29.9 | 31.17 | 32.39 | 32.39 | 32.32 | 27.09 | 28.4 | 29.66 | 29.72 | 29.68 | 0.054496 | 1.4 | 0.31 | 2.37 | 8.65 | 8.63 | 8.63 | 0 | 0.01 | 0.02 | 0.02 | 0.02 | 1 | 2 | 9.5 | 9.5 | 9.5 | 0 | 0 | 0.18 | 0.21 | 0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.093 | 0.711 | 2.721 | 2.736 | 2.722 | 0 | 0.003 | 0.006 | 0.006 | 0.006
CDA | winter | 64.21 | 30.67 | 53 | 2025: 0.99438; 2025: 9.2696; 2026: 11.1541; 2025: 2.1501; 2025: 20.3569; Forecast Maximum Demand (MVA) 2026: 25.46; Forecast Maximum Demand (MVA) 2027: 27.55; Forecast Maximum Demand (MVA) 2028: 28.65; Forecast Maximum Demand (MVA) 2029: 29.44; Forecast Maximum Demand (MVA) 2030: 30.26; Forecast Maximum Demand (MVA) 2026: 23.8; Forecast Maximum Demand (MVA) 2027: 25.88; Forecast Maximum Demand (MVA) 2028: 27.06; Forecast Maximum Demand (MVA) 2029: 27.78; Forecast Maximum Demand (MVA) 2030: 28.49; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CFD | summer | 82.6 | 41.3 | 66 | 0.99915 | 11.9088 | 10.0847 | 2.0912 | 50.8946 | 58.92 | 59.23 | 59.48 | 59.54 | 59.4 | 51.41 | 52.07 | 52.35 | 52.47 | 52.48 | 0.24479 | 10.11 | 332.76 | 346.64 | 353.07 | 342.45 | 359.37 | 0.83 | 0.86 | 0.88 | 0.85 | 0.9 | 70.5 | 74.5 | 71 | 69 | 73.5 | 48.1 | 60.19 | 64.49 | 66.27 | 67.46 | 0.12 | 0.15 | 0.16 | 0.17 | 0.17 | 19.5 | 24 | 25 | 24.5 | 26.5 | 133.498 | 146.125 | 151.064 | 149.124 | 155.033 | 0.333 | 0.363 | 0.376 | 0.374 | 0.389
CFD | winter | 91.2 | 45.6 | 66 | 2025: 0.9999; 2025: 11.9088; 2026: 10.0847; 2025: 1.5126; 2025: 39.034; Forecast Maximum Demand (MVA) 2026: 44.26; Forecast Maximum Demand (MVA) 2027: 45.37; Forecast Maximum Demand (MVA) 2028: 46.64; Forecast Maximum Demand (MVA) 2029: 47.89; Forecast Maximum Demand (MVA) 2030: 49.11; Forecast Maximum Demand (MVA) 2026: 41.12; Forecast Maximum Demand (MVA) 2027: 42.19; Forecast Maximum Demand (MVA) 2028: 43.4; Forecast Maximum Demand (MVA) 2029: 44.61; Forecast Maximum Demand (MVA) 2030: 45.84; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CM | summer | 60.95 | 30.47 | 60 | 0.99966 | 3.1907 | 4.0896 | 6.4161 | 19.0563 | 25.51 | 25.9 | 26.12 | 26.16 | 26.12 | 23.6 | 23.91 | 24.09 | 24.06 | 23.94 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CM | winter | 73.33 | 36.66 | 60 | 2025: 0.99687; 2025: 3.1907; 2026: 4.0896; 2025: 3.3558; 2025: 15.7902; Forecast Maximum Demand (MVA) 2026: 19.17; Forecast Maximum Demand (MVA) 2027: 19.62; Forecast Maximum Demand (MVA) 2028: 20.03; Forecast Maximum Demand (MVA) 2029: 20.27; Forecast Maximum Demand (MVA) 2030: 20.51; Forecast Maximum Demand (MVA) 2026: 18; Forecast Maximum Demand (MVA) 2027: 18.46; Forecast Maximum Demand (MVA) 2028: 18.84; Forecast Maximum Demand (MVA) 2029: 19.12; Forecast Maximum Demand (MVA) 2030: 19.35; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
CRM | summer | 110.28 | 73.52 | 99 | 0.99995 | 64.3961 | 16.6314 | 2.8768 | 75.2954 | 91.49 | 92.44 | 92.87 | 93.03 | 92.68 | 80.18 | 80.88 | 81.38 | 81.5 | 81.07 | 0.090588 | 6.66 | 309.47 | 371.33 | 416.15 | 421.93 | 441.43 | 1.15 | 1.39 | 1.55 | 1.57 | 1.65 | 56 | 62 | 69 | 70.5 | 74 | 10.53 | 16.82 | 24.17 | 30.13 | 31.89 | 0.04 | 0.06 | 0.09 | 0.11 | 0.12 | 5 | 8.5 | 8.5 | 9.5 | 9.5 | 100.212 | 123.173 | 141.764 | 147.67 | 154.752 | 0.373 | 0.459 | 0.528 | 0.548 | 0.579
CRM | winter | 111.2 | 74.13 | 99 | 2025: 0.99676; 2025: 64.3961; 2026: 16.6314; 2025: 1.4027; 2025: 72.8736; Forecast Maximum Demand (MVA) 2026: 79.77; Forecast Maximum Demand (MVA) 2027: 81.5; Forecast Maximum Demand (MVA) 2028: 83.71; Forecast Maximum Demand (MVA) 2029: 85.64; Forecast Maximum Demand (MVA) 2030: 87.55; Forecast Maximum Demand (MVA) 2026: 75.06; Forecast Maximum Demand (MVA) 2027: 77.03; Forecast Maximum Demand (MVA) 2028: 79.36; Forecast Maximum Demand (MVA) 2029: 81.42; Forecast Maximum Demand (MVA) 2030: 83.34; Forecast Maximum Demand (MVA) 2026: 0.012545; Forecast Maximum Demand (MVA) 2026: 0.93
DC | summer | 108.64 | 72.43 | 84 | 0.99995 | 33.7818 | 19.6314 | 3.2466 | 82.3421 | 86.33 | 88.16 | 89.39 | 90.18 | 90.71 | 80.22 | 81.91 | 83.18 | 83.92 | 84.4 | 0.10755 | 7.79 | 101.3 | 154.95 | 208.09 | 246.05 | 311.35 | 0.38 | 0.58 | 0.78 | 0.92 | 1.16 | 25.5 | 34.5 | 42.5 | 49 | 57.5 | 13.31 | 28.16 | 44.83 | 56.9 | 72.42 | 0.05 | 0.11 | 0.17 | 0.21 | 0.27 | 5.5 | 11.5 | 14 | 16 | 21 | 39.707 | 66.197 | 93.808 | 113.645 | 144.099 | 0.149 | 0.251 | 0.353 | 0.423 | 0.537
DC | winter | 113.22 | 75.48 | 84 | 2025: 0.99023; 2025: 33.7818; 2026: 19.6314; 2025: 1.4216; 2025: 60.0834; Forecast Maximum Demand (MVA) 2026: 67.24; Forecast Maximum Demand (MVA) 2027: 70.8; Forecast Maximum Demand (MVA) 2028: 74.52; Forecast Maximum Demand (MVA) 2029: 78.3; Forecast Maximum Demand (MVA) 2030: 82.09; Forecast Maximum Demand (MVA) 2026: 64.27; Forecast Maximum Demand (MVA) 2027: 67.65; Forecast Maximum Demand (MVA) 2028: 71.32; Forecast Maximum Demand (MVA) 2029: 74.93; Forecast Maximum Demand (MVA) 2030: 78.66; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
DMA | summer | 89.59 | 44.8 | 66 | 0.99931 | 26.6771 | 23.1522 | 3.4986 | 37.457 | 48.23 | 49.26 | 49.87 | 50.36 | 50.68 | 42.52 | 43.29 | 43.88 | 44.39 | 44.67 | - | - | 5.23 | 14.99 | 24.01 | 32.52 | 41.86 | 0.01 | 0.04 | 0.06 | 0.08 | 0.1 | 6 | 11.5 | 15 | 20 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.569 | 4.497 | 7.203 | 9.756 | 12.558 | 0.003 | 0.012 | 0.018 | 0.024 | 0.03
DMA | winter | 91.51 | 45.76 | 66 | 2025: 0.99528; 2025: 26.6771; 2026: 23.1522; 2025: 0.90249; 2025: 28.4779; Forecast Maximum Demand (MVA) 2026: 31.48; Forecast Maximum Demand (MVA) 2027: 32.54; Forecast Maximum Demand (MVA) 2028: 33.82; Forecast Maximum Demand (MVA) 2029: 35.01; Forecast Maximum Demand (MVA) 2030: 36.2; Forecast Maximum Demand (MVA) 2026: 29.93; Forecast Maximum Demand (MVA) 2027: 31.01; Forecast Maximum Demand (MVA) 2028: 32.26; Forecast Maximum Demand (MVA) 2029: 33.45; Forecast Maximum Demand (MVA) 2030: 34.62; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
DN | summer | 126.24 | 84.16 | 104 | 0.99422 | 36.5567 | 18.5049 | 2.257 | 70.6725 | 75.02 | 75.61 | 75.96 | 75.07 | 74.04 | 69.49 | 69.88 | 70.26 | 69.35 | 68.29 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DN | winter | 139.24 | 92.82 | 104 | 2025: 0.99811; 2025: 36.5567; 2026: 18.5049; 2025: 3.266; 2025: 64.3534; Forecast Maximum Demand (MVA) 2026: 74.54; Forecast Maximum Demand (MVA) 2027: 76.49; Forecast Maximum Demand (MVA) 2028: 77.62; Forecast Maximum Demand (MVA) 2029: 77.95; Forecast Maximum Demand (MVA) 2030: 78.21; Forecast Maximum Demand (MVA) 2026: 69.91; Forecast Maximum Demand (MVA) 2027: 71.83; Forecast Maximum Demand (MVA) 2028: 72.91; Forecast Maximum Demand (MVA) 2029: 73.26; Forecast Maximum Demand (MVA) 2030: 73.42; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
DSH | summer | 144.84 | 96.56 | 99 | 0.98669 | 11.7446 | 21.9935 | 2.8091 | 58.9565 | 68.51 | 70.5 | 72.56 | 73.29 | 72.99 | 65.77 | 67.77 | 69.78 | 70.58 | 70.26 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DSH | winter | 144.84 | 96.56 | 99 | 2025: 0.99137; 2025: 11.7446; 2026: 21.9935; 2025: 2.8562; 2025: 59.2879; Forecast Maximum Demand (MVA) 2026: 69.73; Forecast Maximum Demand (MVA) 2027: 71.54; Forecast Maximum Demand (MVA) 2028: 73.27; Forecast Maximum Demand (MVA) 2029: 73.42; Forecast Maximum Demand (MVA) 2030: 73.01; Forecast Maximum Demand (MVA) 2026: 66.96; Forecast Maximum Demand (MVA) 2027: 68.76; Forecast Maximum Demand (MVA) 2028: 70.43; Forecast Maximum Demand (MVA) 2029: 70.59; Forecast Maximum Demand (MVA) 2030: 70.22; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
DVY | summer | 131.06 | 87.37 | 99 | 0.97697 | 34.1848 | 11.9272 | 1.0608 | 78.1554 | 88.3 | 94.35 | 101.78 | 102.01 | 101.08 | 83.69 | 89.94 | 97.11 | 97.43 | 96.52 | - | - | 0 | 0 | 2.4 | 2.53 | 0.94 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0.759 | 0.282 | 0 | 0 | 0.003 | 0.003 | 0
DVY | winter | 154.69 | 103.13 | 99 | 2025: 0.98403; 2025: 34.1848; 2026: 11.9272; 2025: 1.4872; 2025: 79.3265; Forecast Maximum Demand (MVA) 2026: 93.54; Forecast Maximum Demand (MVA) 2027: 101.84; Forecast Maximum Demand (MVA) 2028: 105.61; Forecast Maximum Demand (MVA) 2029: 105.69; Forecast Maximum Demand (MVA) 2030: 105.09; Forecast Maximum Demand (MVA) 2026: 88.26; Forecast Maximum Demand (MVA) 2027: 96.57; Forecast Maximum Demand (MVA) 2028: 100.16; Forecast Maximum Demand (MVA) 2029: 100.24; Forecast Maximum Demand (MVA) 2030: 99.85; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
EB | summer | 100.87 | 67.25 | 93 | 0.99884 | 24.9684 | 15.4184 | 2.6119 | 54.3861 | 57.47 | 58.23 | 58.7 | 58.87 | 59 | 53.94 | 54.66 | 54.94 | 54.99 | 54.98 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB | winter | 125.61 | 83.74 | 93 | 2025: 0.99947; 2025: 24.9684; 2026: 15.4184; 2025: 1.7563; 2025: 42.9183; Forecast Maximum Demand (MVA) 2026: 47.16; Forecast Maximum Demand (MVA) 2027: 48.91; Forecast Maximum Demand (MVA) 2028: 50.88; Forecast Maximum Demand (MVA) 2029: 52.81; Forecast Maximum Demand (MVA) 2030: 54.83; Forecast Maximum Demand (MVA) 2026: 44.78; Forecast Maximum Demand (MVA) 2027: 46.5; Forecast Maximum Demand (MVA) 2028: 48.41; Forecast Maximum Demand (MVA) 2029: 50.39; Forecast Maximum Demand (MVA) 2030: 52.36; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
EL | summer | 66.08 | 33.04 | 60 | 0.99182 | 7.7984 | 6.3642 | 1.9757 | 32.6371 | 37.88 | 38.53 | 39.31 | 39.66 | 39.58 | 34.95 | 35.51 | 36.28 | 36.71 | 36.64 | 0.057809 | 1.91 | 0 | 0.39 | 1.41 | 2.01 | 1.8 | 0 | 0 | 0 | 0.01 | 0 | 0.5 | 1 | 1.5 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.117 | 0.423 | 0.603 | 0.54 | 0 | 0 | 0 | 0.003 | 0
EL | winter | 78.91 | 39.45 | 60 | 2025: 0.99694; 2025: 7.7984; 2026: 6.3642; 2025: 1.5106; 2025: 22.2547; Forecast Maximum Demand (MVA) 2026: 24.98; Forecast Maximum Demand (MVA) 2027: 26.13; Forecast Maximum Demand (MVA) 2028: 27.61; Forecast Maximum Demand (MVA) 2029: 28.63; Forecast Maximum Demand (MVA) 2030: 29.47; Forecast Maximum Demand (MVA) 2026: 23.65; Forecast Maximum Demand (MVA) 2027: 24.77; Forecast Maximum Demand (MVA) 2028: 26.21; Forecast Maximum Demand (MVA) 2029: 27.16; Forecast Maximum Demand (MVA) 2030: 27.93; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
EM | summer | 91 | 45.5 | 66 | 0.99873 | 14.1147 | 8.9538 | 3.1324 | 35.5371 | 39.56 | 40.03 | 40.17 | 40.23 | 40.2 | 36.38 | 36.75 | 36.87 | 36.88 | 36.86 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EM | winter | 93.4 | 46.7 | 66 | 2025: 0.99781; 2025: 14.1147; 2026: 8.9538; 2025: 1.539; 2025: 27.3264; Forecast Maximum Demand (MVA) 2026: 32.53; Forecast Maximum Demand (MVA) 2027: 33.38; Forecast Maximum Demand (MVA) 2028: 34.4; Forecast Maximum Demand (MVA) 2029: 35.49; Forecast Maximum Demand (MVA) 2030: 36.59; Forecast Maximum Demand (MVA) 2026: 29.67; Forecast Maximum Demand (MVA) 2027: 30.51; Forecast Maximum Demand (MVA) 2028: 31.53; Forecast Maximum Demand (MVA) 2029: 32.6; Forecast Maximum Demand (MVA) 2030: 33.63; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
EW | summer | 56.76 | 28.38 | 60 | 0.9982 | 4.6943 | 3.826 | 3.2321 | 23.6726 | 28.54 | 29.23 | 29.8 | 30.16 | 30.46 | 25.01 | 25.58 | 26.04 | 26.34 | 26.57 | - | - | 0 | 0.69 | 2.36 | 4.34 | 6.82 | 0 | 0 | 0.01 | 0.01 | 0.02 | 0 | 1 | 2 | 2.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.207 | 0.708 | 1.302 | 2.046 | 0 | 0 | 0.003 | 0.003 | 0.006
EW | winter | 62.63 | 31.32 | 60 | 2025: 0.99487; 2025: 4.6943; 2026: 3.826; 2025: 1.5481; 2025: 24.3197; Forecast Maximum Demand (MVA) 2026: 30.92; Forecast Maximum Demand (MVA) 2027: 32; Forecast Maximum Demand (MVA) 2028: 33.06; Forecast Maximum Demand (MVA) 2029: 34.01; Forecast Maximum Demand (MVA) 2030: 34.93; Forecast Maximum Demand (MVA) 2026: 27.02; Forecast Maximum Demand (MVA) 2027: 28.01; Forecast Maximum Demand (MVA) 2028: 29; Forecast Maximum Demand (MVA) 2029: 29.88; Forecast Maximum Demand (MVA) 2030: 30.72; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
FSH | summer | 91.96 | 61.31 | 93 | 0.99991 | 40.9888 | 20.3609 | 2.0965 | 69.116 | 88.01 | 89 | 89.82 | 90.15 | 89.87 | 72.21 | 73.02 | 73.73 | 74.01 | 73.77 | 0.17779 | 10.9 | 313.51 | 387.94 | 466.56 | 492.98 | 533.2 | 1.17 | 1.45 | 1.74 | 1.84 | 1.99 | 51 | 59 | 67.5 | 72 | 79 | 4.12 | 5.53 | 7.7 | 9.22 | 8.56 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 1.5 | 2 | 3.5 | 4.5 | 4.5 | 96.937 | 120.253 | 145.358 | 154.348 | 165.952 | 0.365 | 0.449 | 0.543 | 0.573 | 0.618
FSH | winter | 108.91 | 72.6 | 93 | 2025: 0.9999; 2025: 40.9888; 2026: 20.3609; 2025: 1.0195; 2025: 56.608; Forecast Maximum Demand (MVA) 2026: 66.91; Forecast Maximum Demand (MVA) 2027: 68.38; Forecast Maximum Demand (MVA) 2028: 70.54; Forecast Maximum Demand (MVA) 2029: 72.15; Forecast Maximum Demand (MVA) 2030: 73.55; Forecast Maximum Demand (MVA) 2026: 59.58; Forecast Maximum Demand (MVA) 2027: 61.3; Forecast Maximum Demand (MVA) 2028: 63.45; Forecast Maximum Demand (MVA) 2029: 65.21; Forecast Maximum Demand (MVA) 2030: 66.92; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
FTN | summer | 90.38 | 45.19 | 66 | 0.99914 | 22.2942 | 18.5976 | 1.9154 | 51.0034 | 59.55 | 60.64 | 61.4 | 61.3 | 61.1 | 55.13 | 56.13 | 56.86 | 56.78 | 56.52 | 0.21996 | 9.94 | 217.68 | 280.89 | 338.62 | 352.16 | 391.26 | 0.54 | 0.7 | 0.84 | 0.88 | 0.98 | 50.5 | 60 | 70.5 | 75.5 | 86 | 64.32 | 92.03 | 120.4 | 124.56 | 133.55 | 0.16 | 0.23 | 0.3 | 0.31 | 0.33 | 22.5 | 31.5 | 37 | 37 | 41.5 | 110.328 | 148.688 | 185.866 | 192.84 | 210.863 | 0.274 | 0.371 | 0.462 | 0.481 | 0.525
FTN | winter | 94.17 | 47.08 | 66 | 2025: 0.99896; 2025: 22.2942; 2026: 18.5976; 2025: 1.5387; 2025: 40.8623; Forecast Maximum Demand (MVA) 2026: 44.58; Forecast Maximum Demand (MVA) 2027: 45.98; Forecast Maximum Demand (MVA) 2028: 47.07; Forecast Maximum Demand (MVA) 2029: 47.76; Forecast Maximum Demand (MVA) 2030: 48.43; Forecast Maximum Demand (MVA) 2026: 42.75; Forecast Maximum Demand (MVA) 2027: 44.18; Forecast Maximum Demand (MVA) 2028: 45.27; Forecast Maximum Demand (MVA) 2029: 46.02; Forecast Maximum Demand (MVA) 2030: 46.74; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
GW | summer | 103.19 | 68.79 | 84 | 0.99566 | 30.4591 | 19.7027 | 2.6265 | 57.9251 | 66.66 | 67.26 | 67.9 | 67.68 | 67.38 | 61.49 | 62.52 | 63.31 | 63.3 | 63.15 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GW | winter | 119.23 | 79.49 | 84 | 2025: 0.99985; 2025: 30.4591; 2026: 19.7027; 2025: 1.9319; 2025: 46.7512; Forecast Maximum Demand (MVA) 2026: 51.92; Forecast Maximum Demand (MVA) 2027: 53.75; Forecast Maximum Demand (MVA) 2028: 55.29; Forecast Maximum Demand (MVA) 2029: 56.67; Forecast Maximum Demand (MVA) 2030: 57.99; Forecast Maximum Demand (MVA) 2026: 48.89; Forecast Maximum Demand (MVA) 2027: 50.81; Forecast Maximum Demand (MVA) 2028: 52.52; Forecast Maximum Demand (MVA) 2029: 53.85; Forecast Maximum Demand (MVA) 2030: 55.12; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
HGS | summer | 77.71 | 38.85 | 66 | 0.99718 | 31.1751 | 14.6135 | 1.0703 | 40.3111 | 66 | 66.68 | 66.87 | 67.09 | 66.66 | 51.1 | 51.39 | 51.57 | 51.74 | 51.58 | 0.31532 | 12.25 | 562.29 | 650.17 | 708.98 | 719.7 | 793.43 | 1.4 | 1.62 | 1.77 | 1.79 | 1.98 | 82.5 | 95 | 107 | 110 | 128 | 16.4 | 18.39 | 20.63 | 22.55 | 23.64 | 0.04 | 0.05 | 0.05 | 0.06 | 0.06 | 6.5 | 7.5 | 8 | 10 | 10 | 180.167 | 207.924 | 227.135 | 231.695 | 254.577 | 0.448 | 0.521 | 0.566 | 0.579 | 0.636
HGS | winter | 90.38 | 45.19 | 66 | 2025: 0.99997; 2025: 31.1751; 2026: 14.6135; 2025: 1.5208; 2025: 38.573; Forecast Maximum Demand (MVA) 2026: 53.03; Forecast Maximum Demand (MVA) 2027: 53.32; Forecast Maximum Demand (MVA) 2028: 53.65; Forecast Maximum Demand (MVA) 2029: 53.64; Forecast Maximum Demand (MVA) 2030: 53.62; Forecast Maximum Demand (MVA) 2026: 42.45; Forecast Maximum Demand (MVA) 2027: 43.16; Forecast Maximum Demand (MVA) 2028: 44.36; Forecast Maximum Demand (MVA) 2029: 45.37; Forecast Maximum Demand (MVA) 2030: 46.25; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
HT | summer | 92.13 | 61.42 | 84 | 0.98876 | 15.7623 | 26.8666 | 2.9427 | 45.0449 | 52.65 | 55.85 | 60 | 59.36 | 58.3 | 48.39 | 51.74 | 55.86 | 55.49 | 54.52 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HT | winter | 109.26 | 72.84 | 84 | 2025: 0.99627; 2025: 15.7623; 2026: 26.8666; 2025: 1.5898; 2025: 41.4555; Forecast Maximum Demand (MVA) 2026: 45.81; Forecast Maximum Demand (MVA) 2027: 52.15; Forecast Maximum Demand (MVA) 2028: 54.8; Forecast Maximum Demand (MVA) 2029: 55.54; Forecast Maximum Demand (MVA) 2030: 56.19; Forecast Maximum Demand (MVA) 2026: 44.19; Forecast Maximum Demand (MVA) 2027: 50.39; Forecast Maximum Demand (MVA) 2028: 53; Forecast Maximum Demand (MVA) 2029: 53.75; Forecast Maximum Demand (MVA) 2030: 54.37; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
K | summer | 73.16 | 36.58 | 60 | 0.99917 | 12.4823 | 7.127 | 2.106 | 37.2247 | 44.5 | 45.19 | 45.35 | 45.41 | 45.39 | 40.2 | 40.52 | 40.6 | 40.63 | 40.53 | 0.098961 | 3.62 | 30.8 | 40.87 | 41.82 | 42.56 | 41.51 | 0.08 | 0.1 | 0.1 | 0.11 | 0.1 | 16 | 19.5 | 19.5 | 19 | 19 | 1.48 | 1.99 | 1.98 | 2.01 | 1.85 | 0 | 0 | 0 | 0.01 | 0 | 2 | 2 | 2 | 1.5 | 1.5 | 10.276 | 13.654 | 13.932 | 14.175 | 13.748 | 0.024 | 0.03 | 0.03 | 0.04 | 0.03
K | winter | 80.33 | 40.16 | 60 | 2025: 0.99902; 2025: 12.4823; 2026: 7.127; 2025: 1.5817; 2025: 27.7237; Forecast Maximum Demand (MVA) 2026: 34.5; Forecast Maximum Demand (MVA) 2027: 35.04; Forecast Maximum Demand (MVA) 2028: 35.73; Forecast Maximum Demand (MVA) 2029: 36.43; Forecast Maximum Demand (MVA) 2030: 37.01; Forecast Maximum Demand (MVA) 2026: 31.96; Forecast Maximum Demand (MVA) 2027: 32.55; Forecast Maximum Demand (MVA) 2028: 33.3; Forecast Maximum Demand (MVA) 2029: 34.02; Forecast Maximum Demand (MVA) 2030: 34.7; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
KBH | summer | 45.81 | 0 | 33 | 0.99999 | 19.3205 | 33.8719 | 1.9378 | 29.8 | 33.91 | 35.57 | 37.37 | 38.25 | 38.71 | 31.2 | 32.87 | 34.78 | 35.64 | 36.07 | 1 | 31.2 | 109498.2969 | 121344.0938 | 132773.9531 | 138329.7031 | 142954.6406 | 136.87 | 151.68 | 165.97 | 172.91 | 178.69 | 8750.5 | 8752.5 | 8756 | 8755.5 | 8755 | 91937.3203 | 102897.5625 | 112661.4062 | 116766.9062 | 119493.6562 | 114.92 | 128.62 | 140.83 | 145.96 | 149.37 | 8730.5 | 8744 | 8747.5 | 8746 | 8743 | 97205.6133 | 108431.5219 | 118695.1703 | 123235.7453 | 126531.9516 | 121.505 | 135.538 | 148.372 | 154.045 | 158.166
KBH | winter | 48.28 | 0 | 33 | 2025: 0.99857; 2025: 19.3205; 2026: 33.8719; 2025: 2.7325; 2025: 27.7077; Forecast Maximum Demand (MVA) 2026: 32.32; Forecast Maximum Demand (MVA) 2027: 34.93; Forecast Maximum Demand (MVA) 2028: 37.18; Forecast Maximum Demand (MVA) 2029: 38.57; Forecast Maximum Demand (MVA) 2030: 39.8; Forecast Maximum Demand (MVA) 2026: 30.77; Forecast Maximum Demand (MVA) 2027: 33.33; Forecast Maximum Demand (MVA) 2028: 35.5; Forecast Maximum Demand (MVA) 2029: 36.85; Forecast Maximum Demand (MVA) 2030: 37.96; Forecast Maximum Demand (MVA) 2026: 1; Forecast Maximum Demand (MVA) 2026: 30.77
LD | summer | 100.18 | 66.79 | 93 | 0.99392 | 34.2166 | 23.8495 | 3.0256 | 48.9134 | 52.48 | 53.41 | 54.45 | 54.68 | 54.39 | 47.84 | 48.72 | 49.85 | 50.21 | 49.91 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LD | winter | 122.25 | 81.5 | 93 | 2025: 0.99949; 2025: 34.2166; 2026: 23.8495; 2025: 1.4202; 2025: 40.4172; Forecast Maximum Demand (MVA) 2026: 42.19; Forecast Maximum Demand (MVA) 2027: 44.24; Forecast Maximum Demand (MVA) 2028: 46.5; Forecast Maximum Demand (MVA) 2029: 48.09; Forecast Maximum Demand (MVA) 2030: 49.56; Forecast Maximum Demand (MVA) 2026: 40.45; Forecast Maximum Demand (MVA) 2027: 42.53; Forecast Maximum Demand (MVA) 2028: 44.72; Forecast Maximum Demand (MVA) 2029: 46.24; Forecast Maximum Demand (MVA) 2030: 47.64; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
LWN | summer | 89.95 | 44.98 | 66 | 0.99877 | 25.5749 | 26.5994 | 3.0768 | 45.9262 | 53.61 | 54.34 | 54.86 | 54.86 | 54.98 | 48.91 | 49.53 | 50 | 50.25 | 50.27 | 0.087372 | 3.93 | 102.8 | 136.97 | 167.88 | 162.4 | 185.39 | 0.26 | 0.34 | 0.42 | 0.4 | 0.46 | 39 | 45 | 52.5 | 50.5 | 56.5 | 8.67 | 14.41 | 20.31 | 23.83 | 25.25 | 0.02 | 0.04 | 0.05 | 0.06 | 0.06 | 7 | 11 | 12 | 13.5 | 14 | 36.909 | 51.178 | 64.581 | 65.401 | 73.292 | 0.092 | 0.13 | 0.161 | 0.162 | 0.18
LWN | winter | 91.1 | 45.55 | 66 | 2025: 0.99885; 2025: 25.5749; 2026: 26.5994; 2025: 1.1888; 2025: 34.6438; Forecast Maximum Demand (MVA) 2026: 38.48; Forecast Maximum Demand (MVA) 2027: 39.59; Forecast Maximum Demand (MVA) 2028: 40.91; Forecast Maximum Demand (MVA) 2029: 42.24; Forecast Maximum Demand (MVA) 2030: 43.6; Forecast Maximum Demand (MVA) 2026: 36.69; Forecast Maximum Demand (MVA) 2027: 37.89; Forecast Maximum Demand (MVA) 2028: 39.37; Forecast Maximum Demand (MVA) 2029: 40.79; Forecast Maximum Demand (MVA) 2030: 42.19; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
M | summer | 78.96 | 52.64 | 87 | 0.99359 | 15.1827 | 5.21 | 2.8727 | 36.5717 | 39.28 | 40.33 | 41.33 | 41.74 | 41.83 | 35.92 | 36.93 | 37.93 | 38.3 | 38.37 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
M | winter | 82.65 | 55.1 | 87 | 2025: 0.99869; 2025: 15.1827; 2026: 5.21; 2025: 1.2982; 2025: 29.7425; Forecast Maximum Demand (MVA) 2026: 32.29; Forecast Maximum Demand (MVA) 2027: 33.87; Forecast Maximum Demand (MVA) 2028: 35.3; Forecast Maximum Demand (MVA) 2029: 36.25; Forecast Maximum Demand (MVA) 2030: 37.18; Forecast Maximum Demand (MVA) 2026: 30.39; Forecast Maximum Demand (MVA) 2027: 31.93; Forecast Maximum Demand (MVA) 2028: 33.33; Forecast Maximum Demand (MVA) 2029: 34.31; Forecast Maximum Demand (MVA) 2030: 35.17; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MC | summer | 82.35 | 54.9 | 87 | 0.98957 | 22.935 | 15.1224 | 1.4282 | 56.2551 | 60.52 | 62.19 | 63.7 | 63.6 | 63.19 | 56.05 | 57.64 | 59.23 | 59.23 | 58.83 | 0.020947 | 1.15 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MC | winter | 96.99 | 64.66 | 87 | 2025: 0.97605; 2025: 22.935; 2026: 15.1224; 2025: 1.4828; 2025: 51.9011; Forecast Maximum Demand (MVA) 2026: 60.07; Forecast Maximum Demand (MVA) 2027: 62.55; Forecast Maximum Demand (MVA) 2028: 63.97; Forecast Maximum Demand (MVA) 2029: 64.33; Forecast Maximum Demand (MVA) 2030: 64.59; Forecast Maximum Demand (MVA) 2026: 57.14; Forecast Maximum Demand (MVA) 2027: 59.51; Forecast Maximum Demand (MVA) 2028: 60.95; Forecast Maximum Demand (MVA) 2029: 61.34; Forecast Maximum Demand (MVA) 2030: 61.55; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MGE | summer | 111.63 | 74.42 | 99 | 0.99944 | 38.3959 | 20.1141 | 2.0998 | 69.3826 | 77.89 | 78.39 | 78.98 | 79.05 | 78.25 | 72.61 | 73.19 | 73.68 | 73.69 | 73.01 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MGE | winter | 126.66 | 84.44 | 99 | 2025: 0.99696; 2025: 38.3959; 2026: 20.1141; 2025: 1.4225; 2025: 57.6703; Forecast Maximum Demand (MVA) 2026: 63.78; Forecast Maximum Demand (MVA) 2027: 65.53; Forecast Maximum Demand (MVA) 2028: 67.57; Forecast Maximum Demand (MVA) 2029: 68.99; Forecast Maximum Demand (MVA) 2030: 70.18; Forecast Maximum Demand (MVA) 2026: 60.95; Forecast Maximum Demand (MVA) 2027: 62.58; Forecast Maximum Demand (MVA) 2028: 64.55; Forecast Maximum Demand (MVA) 2029: 65.85; Forecast Maximum Demand (MVA) 2030: 67.01; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MR | summer | 78.69 | 39.35 | 66 | 0.99165 | 18.9022 | 15.3105 | 2.1167 | 49.0512 | 59.55 | 60.07 | 60.1 | 60.26 | 60.23 | 50.92 | 51.42 | 51.52 | 51.56 | 51.51 | 0.29403 | 11.57 | 849.18 | 927.19 | 981.78 | 1011.96 | 1113.58 | 2.12 | 2.31 | 2.45 | 2.52 | 2.78 | 142 | 159.5 | 167 | 178 | 196.5 | 181.93 | 207.82 | 218.69 | 216.87 | 236.39 | 0.45 | 0.52 | 0.55 | 0.54 | 0.59 | 50.5 | 56 | 55 | 54 | 58 | 382.105 | 423.631 | 447.617 | 455.397 | 499.547 | 0.951 | 1.057 | 1.12 | 1.134 | 1.247
MR | winter | 78.69 | 39.35 | 66 | 2025: 0.99941; 2025: 18.9022; 2026: 15.3105; 2025: 1.5968; 2025: 34.6731; Forecast Maximum Demand (MVA) 2026: 43.1; Forecast Maximum Demand (MVA) 2027: 42.44; Forecast Maximum Demand (MVA) 2028: 44.07; Forecast Maximum Demand (MVA) 2029: 45.74; Forecast Maximum Demand (MVA) 2030: 47.44; Forecast Maximum Demand (MVA) 2026: 38.03; Forecast Maximum Demand (MVA) 2027: 39.26; Forecast Maximum Demand (MVA) 2028: 40.77; Forecast Maximum Demand (MVA) 2029: 42.34; Forecast Maximum Demand (MVA) 2030: 43.87; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
MTN | summer | 91.62 | 45.81 | 66 | 0.99859 | 39.2799 | 20.6209 | 3.1069 | 61.7713 | 71.68 | 72.5 | 73.35 | 74.05 | 73.67 | 64.91 | 65.63 | 66.43 | 67.01 | 66.68 | 0.41694 | 19.1 | 1696.3 | 2180.8401 | 2887.4299 | 3534.3799 | 3902.3899 | 4.23 | 5.44 | 7.2 | 8.81 | 9.73 | 295 | 388 | 517.5 | 635 | 697.5 | 579.02 | 716.34 | 913.67 | 1056.78 | 1151.21 | 1.44 | 1.79 | 2.28 | 2.64 | 2.87 | 112.5 | 137.5 | 177 | 217.5 | 234 | 914.204 | 1155.69 | 1505.798 | 1800.06 | 1976.5639 | 2.277 | 2.885 | 3.756 | 4.491 | 4.928
MTN | winter | 96.56 | 48.28 | 66 | 2025: 0.99972; 2025: 39.2799; 2026: 20.6209; 2025: 1.1252; 2025: 51.374; Forecast Maximum Demand (MVA) 2026: 56.38; Forecast Maximum Demand (MVA) 2027: 57.61; Forecast Maximum Demand (MVA) 2028: 59.57; Forecast Maximum Demand (MVA) 2029: 60.64; Forecast Maximum Demand (MVA) 2030: 61.28; Forecast Maximum Demand (MVA) 2026: 53.3; Forecast Maximum Demand (MVA) 2027: 54.48; Forecast Maximum Demand (MVA) 2028: 56.38; Forecast Maximum Demand (MVA) 2029: 57.45; Forecast Maximum Demand (MVA) 2030: 58.17; Forecast Maximum Demand (MVA) 2026: 0.10398; Forecast Maximum Demand (MVA) 2026: 5.02
NB | summer | 90.43 | 45.22 | 66 | 0.9915 | 12.93 | 7.5605 | 1.5374 | 47.1406 | 51.18 | 51.79 | 52.15 | 52.06 | 51.8 | 44.71 | 45.18 | 45.42 | 45.31 | 45 | - | - | 2.79 | 3.74 | 4.54 | 4.49 | 3.92 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 1.5 | 2 | 2.5 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.837 | 1.122 | 1.362 | 1.347 | 1.176 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003
NB | winter | 99.07 | 49.54 | 66 | 2025: 0.99953; 2025: 12.93; 2026: 7.5605; 2025: 1.4262; 2025: 32.4625; Forecast Maximum Demand (MVA) 2026: 36.78; Forecast Maximum Demand (MVA) 2027: 38; Forecast Maximum Demand (MVA) 2028: 39.2; Forecast Maximum Demand (MVA) 2029: 40.37; Forecast Maximum Demand (MVA) 2030: 41.47; Forecast Maximum Demand (MVA) 2026: 33.88; Forecast Maximum Demand (MVA) 2027: 35.09; Forecast Maximum Demand (MVA) 2028: 36.3; Forecast Maximum Demand (MVA) 2029: 37.45; Forecast Maximum Demand (MVA) 2030: 38.52; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
NO | summer | 109.57 | 73.05 | 90 | 0.99858 | 35.6278 | 6.3953 | 6.0288 | 34.878 | 38.83 | 39.73 | 40.32 | 40.31 | 40.2 | 36.34 | 37.07 | 37.63 | 37.6 | 37.45 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NO | winter | 128.85 | 85.9 | 90 | 2025: 0.99943; 2025: 35.6278; 2026: 6.3953; 2025: 2.1223; 2025: 30.5555; Forecast Maximum Demand (MVA) 2026: 36.28; Forecast Maximum Demand (MVA) 2027: 37.34; Forecast Maximum Demand (MVA) 2028: 37.96; Forecast Maximum Demand (MVA) 2029: 38.36; Forecast Maximum Demand (MVA) 2030: 38.74; Forecast Maximum Demand (MVA) 2026: 33.49; Forecast Maximum Demand (MVA) 2027: 34.52; Forecast Maximum Demand (MVA) 2028: 35.14; Forecast Maximum Demand (MVA) 2029: 35.49; Forecast Maximum Demand (MVA) 2030: 35.82; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
NP | summer | 105.91 | 70.61 | 90 | 0.99687 | 28.8732 | 20.723 | 3.1038 | 53.8745 | 55.84 | 56.63 | 57.21 | 57.61 | 57.68 | 53.06 | 53.77 | 54.3 | 54.67 | 54.75 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NP | winter | 115.06 | 76.71 | 90 | 2025: 0.99961; 2025: 28.8732; 2026: 20.723; 2025: 1.4427; 2025: 47.6176; Forecast Maximum Demand (MVA) 2026: 50.12; Forecast Maximum Demand (MVA) 2027: 51.47; Forecast Maximum Demand (MVA) 2028: 53.26; Forecast Maximum Demand (MVA) 2029: 54.93; Forecast Maximum Demand (MVA) 2030: 56.47; Forecast Maximum Demand (MVA) 2026: 48.35; Forecast Maximum Demand (MVA) 2027: 49.68; Forecast Maximum Demand (MVA) 2028: 51.45; Forecast Maximum Demand (MVA) 2029: 53.06; Forecast Maximum Demand (MVA) 2030: 54.54; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
NW | summer | 132.44 | 88.29 | 99 | 0.99915 | 28.1572 | 23.1373 | 2.487 | 57.1181 | 62.01 | 62.99 | 63.71 | 63.96 | 64.16 | 57.05 | 57.78 | 58.28 | 58.34 | 58.32 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NW | winter | 139.05 | 92.7 | 99 | 2025: 0.99986; 2025: 28.1572; 2026: 23.1373; 2025: 1.6109; 2025: 46.4492; Forecast Maximum Demand (MVA) 2026: 53.47; Forecast Maximum Demand (MVA) 2027: 55.55; Forecast Maximum Demand (MVA) 2028: 57.91; Forecast Maximum Demand (MVA) 2029: 60.39; Forecast Maximum Demand (MVA) 2030: 63.06; Forecast Maximum Demand (MVA) 2026: 49.24; Forecast Maximum Demand (MVA) 2027: 51.41; Forecast Maximum Demand (MVA) 2028: 53.93; Forecast Maximum Demand (MVA) 2029: 56.57; Forecast Maximum Demand (MVA) 2030: 59.41; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
OAK | summer | 128.53 | 85.68 | 99 | 0.99945 | 13.094 | 4.3696 | 2.9052 | 39.9494 | 43.64 | 44.52 | 45.83 | 47.48 | 47.57 | 38 | 38.62 | 40.05 | 41.42 | 41.49 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OAK | winter | 136.75 | 91.17 | 99 | 2025: 0.99094; 2025: 13.094; 2026: 4.3696; 2025: 2.2474; 2025: 24.9259; Forecast Maximum Demand (MVA) 2026: 32.3; Forecast Maximum Demand (MVA) 2027: 34.01; Forecast Maximum Demand (MVA) 2028: 36.98; Forecast Maximum Demand (MVA) 2029: 38.73; Forecast Maximum Demand (MVA) 2030: 40.09; Forecast Maximum Demand (MVA) 2026: 28.18; Forecast Maximum Demand (MVA) 2027: 29.94; Forecast Maximum Demand (MVA) 2028: 32.99; Forecast Maximum Demand (MVA) 2029: 34.93; Forecast Maximum Demand (MVA) 2030: 36.47; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
OE | summer | 62.3 | 31.15 | 60 | 0.98999 | 5.2224 | 5.3061 | 2.1577 | 13.3057 | 15.35 | 16.38 | 17.33 | 17.36 | 17.34 | 13.92 | 14.91 | 15.95 | 15.98 | 15.94 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OE | winter | 62.3 | 31.15 | 60 | 2025: 0.99426; 2025: 5.2224; 2026: 5.3061; 2025: 3.2988; 2025: 12.1391; Forecast Maximum Demand (MVA) 2026: 14.7; Forecast Maximum Demand (MVA) 2027: 16.2; Forecast Maximum Demand (MVA) 2028: 16.83; Forecast Maximum Demand (MVA) 2029: 17.07; Forecast Maximum Demand (MVA) 2030: 17.29; Forecast Maximum Demand (MVA) 2026: 13.98; Forecast Maximum Demand (MVA) 2027: 15.45; Forecast Maximum Demand (MVA) 2028: 16.14; Forecast Maximum Demand (MVA) 2029: 16.39; Forecast Maximum Demand (MVA) 2030: 16.62; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
OR | summer | 64.25 | 32.12 | 54 | 0.99681 | 13.5068 | 9.4637 | 2.4735 | 36.9437 | 41.15 | 42.05 | 42.37 | 42.63 | 42.75 | 35.91 | 36.91 | 37.8 | 38.11 | 38.24 | 0.118 | 3.79 | 39.18 | 60.57 | 73.12 | 85.4 | 100.45 | 0.1 | 0.15 | 0.18 | 0.21 | 0.25 | 21 | 28 | 32 | 37 | 45.5 | 0.39 | 1.97 | 3.82 | 5.05 | 5.94 | 0 | 0 | 0.01 | 0.01 | 0.01 | 1 | 2 | 2.5 | 5 | 6.5 | 12.027 | 19.55 | 24.61 | 29.155 | 34.293 | 0.03 | 0.045 | 0.061 | 0.07 | 0.082
OR | winter | 73.99 | 36.99 | 54 | 2025: 0.99861; 2025: 13.5068; 2026: 9.4637; 2025: 1.367; 2025: 27.3708; Forecast Maximum Demand (MVA) 2026: 31.56; Forecast Maximum Demand (MVA) 2027: 33.66; Forecast Maximum Demand (MVA) 2028: 35.63; Forecast Maximum Demand (MVA) 2029: 37.52; Forecast Maximum Demand (MVA) 2030: 39.36; Forecast Maximum Demand (MVA) 2026: 28.39; Forecast Maximum Demand (MVA) 2027: 30.28; Forecast Maximum Demand (MVA) 2028: 32; Forecast Maximum Demand (MVA) 2029: 33.61; Forecast Maximum Demand (MVA) 2030: 35.23; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
RBD | summer | 91.23 | 45.62 | 66 | 0.9998 | 23.7711 | 16.6809 | 3.0002 | 37.8356 | 45.68 | 46.11 | 46.28 | 46.4 | 46.25 | 42.78 | 43.26 | 43.42 | 43.57 | 43.48 | - | - | 0 | 0.13 | 0.26 | 0.43 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039 | 0.078 | 0.129 | 0.075 | 0 | 0 | 0 | 0 | 0
RBD | winter | 91.93 | 45.96 | 66 | 2025: 0.99796; 2025: 23.7711; 2026: 16.6809; 2025: 1.0281; 2025: 30.0059; Forecast Maximum Demand (MVA) 2026: 32.44; Forecast Maximum Demand (MVA) 2027: 33.02; Forecast Maximum Demand (MVA) 2028: 33.85; Forecast Maximum Demand (MVA) 2029: 34.68; Forecast Maximum Demand (MVA) 2030: 35.45; Forecast Maximum Demand (MVA) 2026: 31.21; Forecast Maximum Demand (MVA) 2027: 31.77; Forecast Maximum Demand (MVA) 2028: 32.57; Forecast Maximum Demand (MVA) 2029: 33.36; Forecast Maximum Demand (MVA) 2030: 34.13; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SH | summer | 22.19 | 11.09 | 20 | 0.99348 | 2.5405 | 0 | 1.4003 | 7.2084 | 7.81 | 7.95 | 8.06 | 8.15 | 8.21 | 7.15 | 7.28 | 7.37 | 7.46 | 7.52 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SH | winter | 25.38 | 12.69 | 20 | 2025: 0.99941; 2025: 2.5405; 2026: 0; 2025: 1.0241; 2025: 5.3757; Forecast Maximum Demand (MVA) 2026: 6.5; Forecast Maximum Demand (MVA) 2027: 6.83; Forecast Maximum Demand (MVA) 2028: 7.21; Forecast Maximum Demand (MVA) 2029: 7.61; Forecast Maximum Demand (MVA) 2030: 8.03; Forecast Maximum Demand (MVA) 2026: 5.86; Forecast Maximum Demand (MVA) 2027: 6.16; Forecast Maximum Demand (MVA) 2028: 6.54; Forecast Maximum Demand (MVA) 2029: 6.92; Forecast Maximum Demand (MVA) 2030: 7.29; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SR | summer | 67.75 | 33.87 | 54 | 0.9985 | 11.1746 | 11.4004 | 2.1432 | 33.4482 | 36.36 | 36.85 | 37.14 | 37.35 | 37.48 | 32.53 | 32.94 | 33.18 | 33.37 | 33.48 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SR | winter | 80.99 | 40.5 | 54 | 2025: 0.99972; 2025: 11.1746; 2026: 11.4004; 2025: 1.2359; 2025: 24.978; Forecast Maximum Demand (MVA) 2026: 29.17; Forecast Maximum Demand (MVA) 2027: 29.94; Forecast Maximum Demand (MVA) 2028: 30.93; Forecast Maximum Demand (MVA) 2029: 31.91; Forecast Maximum Demand (MVA) 2030: 32.88; Forecast Maximum Demand (MVA) 2026: 26.57; Forecast Maximum Demand (MVA) 2027: 27.34; Forecast Maximum Demand (MVA) 2028: 28.34; Forecast Maximum Demand (MVA) 2029: 29.33; Forecast Maximum Demand (MVA) 2030: 30.29; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SS | summer | 79.87 | 39.93 | 66 | 0.99966 | 30.1479 | 19.8961 | 1.3203 | 35.0675 | 46.67 | 46.91 | 47.49 | 47.07 | 46.61 | 32.4 | 33.4 | 34.5 | 34.59 | 34.54 | - | - | 3.48 | 3.77 | 4.75 | 3.94 | 3.26 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 1.5 | 1.5 | 2 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.044 | 1.131 | 1.425 | 1.182 | 0.978 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003
SS | winter | 90.77 | 45.38 | 66 | 2025: 0.99952; 2025: 30.1479; 2026: 19.8961; 2025: 1.5047; 2025: 31.2273; Forecast Maximum Demand (MVA) 2026: 31.82; Forecast Maximum Demand (MVA) 2027: 33.13; Forecast Maximum Demand (MVA) 2028: 33.76; Forecast Maximum Demand (MVA) 2029: 34.37; Forecast Maximum Demand (MVA) 2030: 35.03; Forecast Maximum Demand (MVA) 2026: 25.68; Forecast Maximum Demand (MVA) 2027: 27.22; Forecast Maximum Demand (MVA) 2028: 28.1; Forecast Maximum Demand (MVA) 2029: 28.76; Forecast Maximum Demand (MVA) 2030: 29.36; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
STO | summer | 72.04 | 36.02 | 66 | 0.95248 | 27.4985 | 13.2604 | 0.89586 | 40.5782 | 50.23 | 51.28 | 52.09 | 52.45 | 52.44 | 42.88 | 43.81 | 44.48 | 44.76 | 44.86 | 0.19045 | 6.86 | 501.2 | 724.9 | 996.99 | 1111.97 | 1334.16 | 1.25 | 1.81 | 2.49 | 2.77 | 3.33 | 127 | 177 | 240 | 276.5 | 328 | 49.87 | 95.59 | 154.28 | 171.37 | 219.26 | 0.12 | 0.24 | 0.38 | 0.43 | 0.55 | 27.5 | 44 | 57.5 | 61.5 | 73.5 | 185.269 | 284.383 | 407.093 | 453.55 | 553.73 | 0.459 | 0.711 | 1.013 | 1.132 | 1.384
STO | winter | 72.04 | 36.02 | 66 | 2025: 0.99862; 2025: 27.4985; 2026: 13.2604; 2025: 1.0012; 2025: 27.5068; Forecast Maximum Demand (MVA) 2026: 31.65; Forecast Maximum Demand (MVA) 2027: 32.64; Forecast Maximum Demand (MVA) 2028: 33.69; Forecast Maximum Demand (MVA) 2029: 34.81; Forecast Maximum Demand (MVA) 2030: 35.69; Forecast Maximum Demand (MVA) 2026: 28.08; Forecast Maximum Demand (MVA) 2027: 29.15; Forecast Maximum Demand (MVA) 2028: 30.17; Forecast Maximum Demand (MVA) 2029: 31.05; Forecast Maximum Demand (MVA) 2030: 31.85; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SV | summer | 159.43 | 119.57 | 66 | 0.98869 | 15.2168 | 26.8536 | 5.7044 | 39.6641 | 50.64 | 51.38 | 51.58 | 51.42 | 51.18 | 45.46 | 46.34 | 46.77 | 46.68 | 46.4 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SV | winter | 185.4 | 139.05 | 66 | 2025: 0.99898; 2025: 15.2168; 2026: 26.8536; 2025: 5.3191; 2025: 36.1127; Forecast Maximum Demand (MVA) 2026: 43.03; Forecast Maximum Demand (MVA) 2027: 44.07; Forecast Maximum Demand (MVA) 2028: 44.73; Forecast Maximum Demand (MVA) 2029: 45.05; Forecast Maximum Demand (MVA) 2030: 45.27; Forecast Maximum Demand (MVA) 2026: 39.31; Forecast Maximum Demand (MVA) 2027: 40.37; Forecast Maximum Demand (MVA) 2028: 40.99; Forecast Maximum Demand (MVA) 2029: 41.36; Forecast Maximum Demand (MVA) 2030: 41.73; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
SVW | summer | 159.43 | 119.57 | 66 | 0.98821 | 29.6561 | 26.8536 | 9.4938 | 46.1701 | 53.2 | 54.2 | 54.82 | 54.61 | 54.32 | 49.39 | 50.36 | 50.92 | 50.7 | 50.41 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SVW | winter | 185.4 | 139.05 | 66 | 2025: 0.99745; 2025: 29.6561; 2026: 26.8536; 2025: 2.5136; 2025: 42.8331; Forecast Maximum Demand (MVA) 2026: 59.77; Forecast Maximum Demand (MVA) 2027: 61.08; Forecast Maximum Demand (MVA) 2028: 61.79; Forecast Maximum Demand (MVA) 2029: 62.1; Forecast Maximum Demand (MVA) 2030: 62.2; Forecast Maximum Demand (MVA) 2026: 54.1; Forecast Maximum Demand (MVA) 2027: 55.45; Forecast Maximum Demand (MVA) 2028: 56.08; Forecast Maximum Demand (MVA) 2029: 56.44; Forecast Maximum Demand (MVA) 2030: 56.74; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
WD | summer | 93.65 | 62.44 | 87 | 0.99405 | 8.175 | 4.7746 | 2.6812 | 51.8847 | 58.35 | 59.41 | 59.83 | 60.19 | 60.38 | 54.22 | 55.21 | 55.56 | 55.87 | 55.99 | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WD | winter | 104.15 | 69.43 | 87 | 2025: 0.9992; 2025: 8.175; 2026: 4.7746; 2025: 1.7693; 2025: 36.0099; Forecast Maximum Demand (MVA) 2026: 41.35; Forecast Maximum Demand (MVA) 2027: 42.29; Forecast Maximum Demand (MVA) 2028: 43.51; Forecast Maximum Demand (MVA) 2029: 44.69; Forecast Maximum Demand (MVA) 2030: 45.87; Forecast Maximum Demand (MVA) 2026: 38.68; Forecast Maximum Demand (MVA) 2027: 39.64; Forecast Maximum Demand (MVA) 2028: 40.81; Forecast Maximum Demand (MVA) 2029: 41.96; Forecast Maximum Demand (MVA) 2030: 43.08; Forecast Maximum Demand (MVA) 2026: -; Forecast Maximum Demand (MVA) 2026: -
a