## Intro
United Energy (UE) 2025 Distribution System Limitation Template
This Distribution Systems Limitations template is intended to make the Distribution Annual Planning Report (DAPR) limitation data more accessible and usable. Any information provided in this System Limitations template should be read in conjunction with the United Energy 2025 DAPR. It should also be noted that the information in this template and the DAPR are based on high-level risk assessments produced for the DAPR. As such the numbers are indicative and subject to change. Therefore the information in this template should not be used to make investment decisions, and should only be used to assist in discussions with United Energy. Finalised data will be produced in a detailed risk assessment conducted at the RIT-D or business case stage. However United Energy invites interested parties to submit their proposals or to engage in joint planning with United Energy as early as possible in order to defer or avoid the proposed augmentation. United Energy also publishes its own Network Limitation maps in order to assist with the visualisation of the limitation data presented within this template and the DAPR. In 2018, United Energy changed the format of the data for the limitations to a commonly developed Energy Networks Australia (ENA) template. This template combines the requirements of the online Australian Renewable Energy Mapping Infrastructure (AREMI) Network Opportunity Maps (NOM) and the Australian Energy Regulator (AER) template requirements in a single, consistent format that is machine readable for very large datasets. This change was made to make the format consistent across the Distribution Businesses. Note that some additional non-critical data fields that are potential additional only applicable to the NOM may be omitted. The data in this template will be updated annually and will be published along with the DAPR. We welcome any feedback to improve the content or usability of this template.

## United Energy Limitations
Owner | Asset Name | Project Name | Asset Code | Network Element | Voltage level (kV) | Rating | [5 empty] | Nameplate Rating | Location |  |  |  | Residential customers affected |  | Business Case | [7 empty] | Demand Reduction required to defer investment by 1 year |  | Emergency Generation |  | Load Transfer capability (MVA) | Power Factor | 10% POE | [14 empty] | 50% POE | [14 empty] | Weighted Expected Energy at Risk (MWh)
[6 empty] | Summer |  |  | Winter |  |  |  | Start |  | End |  |  |  | Constraint Primary Driver | Investment Description | Preferred network investment |  |  |  | Proposed Timing | Annual Deferral Value | [6 empty] | Forecast Minimum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2) |  |  |  |  | Forecast Minimum Demand (MVA) |  |  |  |  | Maximum Load at risk (MVA) (N-1) |  |  |  |  | Maximum Load at risk (MVA) (N-2)
[6 empty] | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) | N Rating (MVA) | N-1 Rating (MVA) | N-2 Rating (MVA) |  | Longitude | Latitude | Longitude | Latitude | Count | Percent |  |  | capital cost ($) | cost accuracy plus | cost accuracy minus | Operating cost ($) |  |  | (MW) | (MVA) | (MW) | (MVA) |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Note on AD1: Lin, Tim: E.g. contracting backup generators in a hospital to become embedded generators during unuasually high peaks
Note on AA2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Lee Conrad, Angelo use WACC value of 3.5% I left the formula below
Note on Y3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Lee Conrad, Angelo this is 1% of total cost , I left the formula below

## Sub-T Aug Sum
Sub transmission line | Season | Line N Import Rating (MVA) | Line Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Hours load is > 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | 50% POE load above N Import Rating (%) | 50% POE load above N Import Rating (MVA) | 50% POE
[8 empty] | Forecast Minimum Demand (MVA) | [6 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
|  |  | 2025 | 2025 | 2026 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
BT-NB | S | 70.9 | 0.9403 | 22.8631 | - | - | 6.7 | 7.4 | 7 | 6.5 | 5.6 | 6.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BT-NB | W | 81.7 | 0.90426 | 22.8631 | - | - | 9.4 | 8.1 | 8.2 | 7.6 | 6.9 | 6.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-OE | S | 65.2 | 0.25 | 5.2224 | - | - | 1.2 | 2.9 | 3.1 | 4 | 3.3 | 2.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-OE | W | 91.5 | 0.94872 | 5.2224 | - | - | 3.9 | 6.3 | 8.4 | 8.4 | 7.8 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN | S | 118.3 | 1 | 36.5567 | - | - | 4.2 | 6.4 | 5.7 | 4.2 | 4.3 | 4.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN | W | 130.3 | 1 | 36.5567 | - | - | 15.8 | 13.4 | 16 | 17.3 | 17.1 | 16.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GW-NO | S | 94.9 | 0.94898 | 66.0868 | - | - | 9.8 | 7.6 | 7.7 | 7.9 | 7.9 | 7.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GW-NO | W | 101.7 | 0.91509 | 66.0868 | - | - | 10.6 | 8 | 8.3 | 8.5 | 8.6 | 8.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-MR | S | 92.6 | 0.88571 | 18.9022 | - | - | 10.5 | 12.1 | 10.6 | 9.2 | 7.8 | 7.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-MR | W | 104.6 | 0.91111 | 18.9022 | - | - | 18 | 14.8 | 14.1 | 12.7 | 11.2 | 9.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN/HPK | S | 117.2 | 0.97222 | 36.5567 | - | - | 3.6 | 4.8 | 4.7 | 4.3 | 4.5 | 4.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DN/HPK | W | 126.3 | 0.9823 | 36.5567 | - | - | 11.3 | 13.2 | 14.8 | 16 | 16.3 | 16.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | S | 117.2 | 0.99438 | 0 | - | - | 17.8 | 21.4 | 21.4 | 21 | 20.6 | 19.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-CL | W | 126.3 | 0.99462 | 0 | - | - | 18.6 | 22.2 | 22.5 | 22.6 | 22.7 | 22.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KBH-M-MC | S | 78.3 | 0.94118 | 57.4382 | - | - | 5.1 | 4.6 | 4.5 | 4 | 4.2 | 5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KBH-M-MC | W | 78.3 | 1 | 57.4382 | - | - | 1.5 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SR-CM | S | 94.9 | 0.89394 | 14.3653 | - | - | 6.6 | 6.1 | 8.9 | 13.1 | 12.4 | 11.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SR-CM | W | 101.7 | 0.97414 | 14.3653 | - | - | 11.6 | 5 | 7.8 | 9.8 | 9.8 | 10.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SV | S | 128 | 0.9881 | 15.2168 | - | - | 16.8 | 15 | 15.5 | 16.4 | 15.9 | 15.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SV | W | 136.6 | 0.97906 | 15.2168 | - | - | 19.1 | 15.8 | 17.3 | 18.1 | 18.4 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-BR | S | 97.2 | 0.94595 | 12.7852 | - | - | 3.7 | 8.2 | 8.7 | 8.9 | 10.6 | 12.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-BR | W | 97.2 | 0.97778 | 12.7852 | - | - | 4.5 | 4.3 | 4.5 | 4.1 | 3.7 | 3.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-CRM | S | 128 | 1 | 64.3961 | - | - | 12.5 | 16.2 | 17.9 | 19.6 | 21.2 | 23.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-CRM | W | 133.7 | 0.77049 | 64.3961 | - | - | 6.1 | 5.3 | 5.1 | 5 | 5.2 | 5.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | S | 90.3 | 0.99435 | 12.4823 | - | - | 17.7 | 20.8 | 20.9 | 20.5 | 20.1 | 19.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-K | W | 104.6 | 1 | 12.4823 | - | - | 18.5 | 21.7 | 21.9 | 22.1 | 22.2 | 22.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SS | S | 108.6 | 0.8625 | 30.1479 | - | - | 8 | 7 | 8.1 | 9.3 | 11.5 | 14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SS | W | 115.5 | 0.65476 | 30.1479 | - | - | 8.4 | 7 | 6.7 | 6 | 5.5 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW1 | S | 12.8 | 0.85714 | 12.6848 | - | - | 0.7 | 1 | 1.2 | 1.5 | 1.8 | 2.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW1 | W | 14.9 | 0.75 | 12.6848 | - | - | 0.4 | 0.8 | 0.8 | 0.8 | 0.9 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | S | 85.7 | 0.90661 | 4.6943 | - | - | 25.7 | 26 | 26.1 | 26.1 | 26.1 | 26 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RTS-EW | W | 101.7 | 0.89961 | 4.6943 | - | - | 25.9 | 26.1 | 26.2 | 26.3 | 26.3 | 26.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M2 | S | 72.6 | 0.82857 | 15.1827 | - | - | 3.5 | 5.8 | 6 | 5.9 | 7 | 8.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M2 | W | 72.6 | 0.95652 | 15.1827 | - | - | 4.6 | 4.5 | 5.2 | 5 | 4.4 | 3.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS2 | S | 88.6 | 1 | 31.1751 | - | - | 29.1 | 37.2 | 38.5 | 38.9 | 39.4 | 40.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS2 | W | 88.6 | 0.99559 | 31.1751 | - | - | 22.7 | 13.1 | 12.8 | 12.5 | 12.8 | 13.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CM-HT | S | 97.2 | 0.90323 | 18.953 | - | - | 6.2 | 4.3 | 5.9 | 9.9 | 9.2 | 8.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CM-HT | W | 109.2 | 0.88764 | 18.953 | - | - | 8.9 | 4 | 6.5 | 8.3 | 8.3 | 8.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS1 | S | 88.6 | 1 | 31.1751 | - | - | 29.1 | 37.2 | 38.5 | 38.9 | 39.4 | 40.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-HGS1 | W | 88.6 | 0.99559 | 31.1751 | - | - | 22.7 | 13.1 | 12.8 | 12.5 | 12.8 | 13.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-CDA | S | 65.2 | 0.25 | 9.2696 | - | - | 1.2 | 2.8 | 3.1 | 4 | 3.2 | 2.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-CDA | W | 91.5 | 0.94872 | 9.2696 | - | - | 3.9 | 6.2 | 8.4 | 8.4 | 7.8 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-CFD | S | 94.9 | 0.94697 | 11.9088 | - | - | 13.2 | 15.8 | 15.1 | 14.6 | 13.8 | 12.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-CFD | W | 98.9 | 0.92442 | 11.9088 | - | - | 17.2 | 16.4 | 16.9 | 17.2 | 16.9 | 16.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M | S | 97.2 | 0.80556 | 15.1827 | - | - | 3.6 | 5.9 | 6.2 | 6 | 7.1 | 8.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-M | W | 97.2 | 0.95745 | 15.1827 | - | - | 4.7 | 4.6 | 5.3 | 5.1 | 4.5 | 4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-NB | S | 92.6 | 0.87736 | 12.93 | - | - | 10.6 | 12.2 | 10.8 | 9.3 | 7.9 | 7.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-NB | W | 108.6 | 0.90608 | 12.93 | - | - | 18.1 | 14.9 | 14.2 | 12.8 | 11.4 | 9.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EB-RD | S | 65.2 | 0.85 | 24.9684 | - | - | 4 | 5.5 | 5 | 4.7 | 4.6 | 4.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EB-RD | W | 77.2 | 0.94805 | 24.9684 | - | - | 7.7 | 8.2 | 7.7 | 7.2 | 6.6 | 5.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NO | S | 128 | 0.95902 | 35.6278 | - | - | 12.2 | 10.8 | 10.5 | 10.2 | 9.3 | 8.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NO | W | 133.7 | 0.96552 | 35.6278 | - | - | 17.4 | 14.3 | 15.1 | 14.9 | 14.3 | 13.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-FTS | S | 94 | 0.39394 | 0 | - | - | 3.3 | 4.4 | 4.9 | 5.9 | 7.3 | 9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-FTS | W | 96 | 0.68889 | 0 | - | - | 4.5 | 5.3 | 5 | 4.9 | 5.3 | 6.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM/EL | S | 100.6 | 1 | 21.9131 | - | - | 8.7 | 10.7 | 9.7 | 8.7 | 7.6 | 6.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM/EL | W | 108.6 | 1 | 21.9131 | - | - | 12.8 | 13.1 | 12.9 | 12.5 | 11.9 | 10.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-BU | S | 100.6 | 0.93651 | 11.4779 | - | - | 6.3 | 7.1 | 6.3 | 5.5 | 4.8 | 4.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-BU | W | 112 | 0.90826 | 11.4779 | - | - | 10.9 | 10.3 | 9.8 | 9.1 | 8.2 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OE-CDA | S | 84 | 0.11111 | 14.492 | - | - | 0.9 | 1.9 | 2 | 2.2 | 2 | 1.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OE-CDA | W | 101.7 | 0.95652 | 14.492 | - | - | 2.3 | 3.9 | 5 | 5.1 | 4.8 | 4.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTS-LWN | S | 100 | 0.97 | 25.5749 | - | - | 10 | 13.4 | 15.5 | 17.6 | 20.2 | 23.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTS-LWN | W | 125.7 | 0 | 25.5749 | - | - | 3.8 | 4.4 | 4.2 | 4.2 | 4.6 | 5.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FSH | S | 84 | 0.39394 | 40.9888 | - | - | 3.3 | 4.4 | 4.9 | 5.9 | 7.2 | 9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FSH | W | 96 | 0.68889 | 40.9888 | - | - | 4.5 | 5.3 | 5 | 4.9 | 5.3 | 6.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM | S | 100.6 | 1 | 14.1147 | - | - | 8.4 | 10.4 | 9.5 | 8.7 | 7.7 | 6.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-EM | W | 108.6 | 0.9916 | 14.1147 | - | - | 11.9 | 12.2 | 12 | 11.8 | 11.3 | 10.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DN-DSH-DVY | S | 128 | 0.9375 | 82.4862 | - | - | 6.4 | 7.6 | 8.3 | 9.2 | 9.3 | 9.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DN-DSH-DVY | W | 136.6 | 0.98462 | 82.4862 | - | - | 19.5 | 7.6 | 8.8 | 9.4 | 9.4 | 9.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-LD | S | 128 | 0.66304 | 34.2166 | - | - | 9.2 | 8.6 | 10.3 | 11.5 | 13.7 | 16.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-LD | W | 133.7 | 0.36905 | 34.2166 | - | - | 8.4 | 7.2 | 7.3 | 7.2 | 6.9 | 7.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SS-NP | S | 84 | 0.74576 | 59.0211 | - | - | 5.9 | 4.9 | 5 | 5.3 | 6.9 | 8.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SS-NP | W | 96.6 | 0.56897 | 59.0211 | - | - | 5.8 | 4.7 | 4.9 | 4.9 | 4.6 | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO2 | S | 56 | 0.25 | 51.2696 | - | - | 0.4 | 0.8 | 0.8 | 0.9 | 1 | 1.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO2 | W | 60 | 0.46667 | 51.2696 | - | - | 1.5 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LD-MGE | S | 80 | 0.37143 | 72.6125 | - | - | 7 | 6.3 | 7.1 | 7.8 | 8.9 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LD-MGE | W | 88.6 | 0.32812 | 72.6125 | - | - | 6.4 | 5.7 | 5.7 | 5.7 | 5.7 | 5.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTN-DMA | S | 128 | 0.86585 | 65.957 | - | - | 8.2 | 11.7 | 13.5 | 15.3 | 17.3 | 19.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTN-DMA | W | 134 | 0.11765 | 65.957 | - | - | 5.1 | 6.2 | 6.4 | 6.9 | 7.6 | 8.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW3 | S | 12.8 | 0.85714 | 12.6848 | - | - | 0.7 | 1 | 1.2 | 1.5 | 1.8 | 2.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-BW3 | W | 15.6 | 0.75 | 12.6848 | - | - | 0.4 | 0.8 | 0.8 | 0.8 | 0.9 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-GW | S | 128 | 0.95902 | 30.4591 | - | - | 12.2 | 10.8 | 10.5 | 10.2 | 9.3 | 8.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-GW | W | 131.5 | 0.97126 | 30.4591 | - | - | 17.4 | 14.4 | 15.1 | 14.9 | 14.3 | 13.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OR | S | 81.7 | 0.87838 | 13.5068 | - | - | 7.4 | 6.7 | 7.1 | 8 | 9.5 | 10.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OR | W | 89.2 | 0.8 | 13.5068 | - | - | 10.5 | 11 | 11.5 | 12 | 12 | 11.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DMA-RBD1 | S | 68.6 | 0.82927 | 50.4483 | - | - | 4.1 | 6.4 | 7.5 | 8.6 | 9.8 | 11.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DMA-RBD1 | W | 68.6 | 0.21429 | 50.4483 | - | - | 4.2 | 4.9 | 5 | 5.4 | 6 | 6.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DMA-RBD2 | S | 70 | 0.82927 | 50.4483 | - | - | 4.1 | 6.4 | 7.5 | 8.6 | 9.8 | 11.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DMA-RBD2 | W | 75 | 0.21951 | 50.4483 | - | - | 4.1 | 4.9 | 5 | 5.4 | 6 | 6.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FTN | S | 76.6 | 0.9661 | 22.2942 | - | - | 5.9 | 8.1 | 9.2 | 10.3 | 11.7 | 13.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTS-FTN | W | 94.3 | 0.82857 | 22.2942 | - | - | 7 | 7.8 | 7.8 | 7.5 | 7.2 | 7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BU-WD | S | 100 | 0.98438 | 19.6529 | - | - | 6.4 | 7.9 | 7.6 | 7.2 | 6.8 | 6.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BU-WD | W | 117.7 | 0.92222 | 19.6529 | - | - | 9 | 9.3 | 9.1 | 8.8 | 8.5 | 8.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EW-SK | S | 86.3 | 0.76793 | 4.6943 | - | - | 23.7 | 23.6 | 23.5 | 23.4 | 23.4 | 23.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EW-SK | W | 91.5 | 0.77447 | 4.6943 | - | - | 23.5 | 23.5 | 23.4 | 23.3 | 23.2 | 23.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-NW | S | 128 | 0.92754 | 28.1572 | - | - | 6.9 | 12.3 | 12.1 | 11.9 | 12 | 12.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-NW | W | 130.3 | 0.94815 | 28.1572 | - | - | 13.5 | 13.1 | 12.7 | 12.1 | 11.5 | 10.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-WD | S | 93.2 | 0.98438 | 8.175 | - | - | 6.4 | 7.9 | 7.6 | 7.2 | 6.8 | 6.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-WD | W | 104.6 | 0.90826 | 8.175 | - | - | 10.9 | 10.3 | 9.8 | 9.1 | 8.5 | 8.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OAK | S | 94.9 | 0.79747 | 13.094 | - | - | 7.9 | 6.7 | 7 | 7.9 | 9.5 | 10.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-OAK | W | 98.9 | 0.80769 | 13.094 | - | - | 10.4 | 10.9 | 11.5 | 12 | 12 | 11.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-HPK | S | 102.3 | 0.92308 | 0 | - | - | 6.5 | 7.7 | 8.2 | 8.7 | 9.1 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-HPK | W | 126.3 | 0.88608 | 0 | - | - | 15.8 | 26.8 | 28.6 | 30.6 | 31.9 | 32.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | S | 91.5 | 0.98214 | 12.4823 | - | - | 11.2 | 11.7 | 11.9 | 12 | 12 | 11.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K-CL | W | 105.7 | 0.98261 | 12.4823 | - | - | 11.5 | 12.2 | 12.4 | 12.6 | 12.8 | 12.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-HT | S | 128 | 0.89535 | 15.7623 | - | - | 8.6 | 7.1 | 9.3 | 13 | 12.4 | 11.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-HT | W | 133.7 | 0.94375 | 15.7623 | - | - | 16 | 7.6 | 9.9 | 11.3 | 10.9 | 10.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BR-MC | S | 90.3 | 1 | 35.7202 | - | - | 2.9 | 6.6 | 6.4 | 5.8 | 6.6 | 7.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BR-MC | W | 90.3 | 1 | 35.7202 | - | - | 3.4 | 2.6 | 3.5 | 3.5 | 3.1 | 2.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CFD-EL | S | 94.9 | 0.96591 | 19.7072 | - | - | 8.8 | 10.3 | 9.8 | 9.1 | 8.3 | 7.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CFD-EL | W | 98.9 | 0.90826 | 19.7072 | - | - | 10.9 | 10.1 | 10.3 | 10.3 | 10 | 9.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC2 | S | 100.6 | 0.28571 | 33.7818 | - | - | 4.9 | 7 | 6.6 | 6.4 | 6.8 | 8.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC2 | W | 108.6 | 0.72727 | 33.7818 | - | - | 8.8 | 10.8 | 10.3 | 9.3 | 8.5 | 7.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH/BW | S | 17.5 | 0.25 | 15.2253 | - | - | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH/BW | W | 19.1 | 1 | 15.2253 | - | - | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OAK-OR | S | 84 | 0.79747 | 26.6007 | - | - | 7.9 | 6.7 | 6.8 | 7.4 | 8 | 8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OAK-OR | W | 98.9 | 0.83117 | 26.6007 | - | - | 7.7 | 8.1 | 8.5 | 9.3 | 9.8 | 9.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MR-BT | S | 75.4 | 0.93023 | 28.8353 | - | - | 8.6 | 9.2 | 8.3 | 7.3 | 5.9 | 4.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MR-BT | W | 81.2 | 0.92913 | 28.8353 | - | - | 12.7 | 11.7 | 11.5 | 10.4 | 9.3 | 8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FSH-MTN | S | 77 | 0.71795 | 80.2687 | - | - | 3.9 | 5.5 | 6.4 | 7.6 | 9 | 10.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FSH-MTN | W | 96 | 0.68889 | 80.2687 | - | - | 4.5 | 5.3 | 5 | 4.9 | 5 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BH-NW | S | 102 | 1 | 39.2309 | - | - | 7.2 | 7.4 | 7.4 | 7.3 | 7.2 | 7.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BH-NW | W | 115 | 0.98889 | 39.2309 | - | - | 9 | 6.9 | 6.8 | 6.9 | 6.9 | 7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SVW | S | 128 | 0.9881 | 29.6561 | - | - | 16.8 | 14.9 | 15.4 | 16.4 | 15.9 | 15.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-SVW | W | 136.6 | 0.97906 | 29.6561 | - | - | 19.1 | 15.8 | 17.3 | 18.1 | 18.4 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH3 | S | 14.3 | 0.25 | 2.5405 | - | - | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTS-SH3 | W | 15.2 | 1 | 2.5405 | - | - | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DSH | S | 128 | 0.92308 | 11.7446 | - | - | 6.5 | 7.7 | 8.3 | 9.2 | 9.3 | 9.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DSH | W | 133.7 | 0.98974 | 11.7446 | - | - | 19.5 | 8.5 | 11.4 | 12.9 | 12.8 | 12.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-FTS2 | S | 94.3 | 0.96296 | 0 | - | - | 8.1 | 10.9 | 12.5 | 14 | 16 | 18.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-FTS2 | W | 123.5 | 0.025641 | 0 | - | - | 3.9 | 4.5 | 4.3 | 4.2 | 4.4 | 4.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-SR | S | 128 | 0.88506 | 11.1746 | - | - | 8.7 | 7.2 | 9.4 | 12.6 | 11.1 | 9.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-SR | W | 133.7 | 0.94375 | 11.1746 | - | - | 16 | 7.6 | 9.9 | 11.3 | 10.9 | 10.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-BH | S | 120 | 1 | 11.0737 | - | - | 7.2 | 12.3 | 12.2 | 12 | 12.1 | 12.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RWTS-BH | W | 132.6 | 0.94815 | 11.0737 | - | - | 13.5 | 13.1 | 12.7 | 12.1 | 11.5 | 10.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-FTS1 | S | 94.3 | 0.96203 | 0 | - | - | 7.9 | 10.7 | 12.2 | 13.7 | 15.6 | 18 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CBTS-FTS1 | W | 123.5 | 0.026316 | 0 | - | - | 3.8 | 4.4 | 4.2 | 4.1 | 4.3 | 4.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NP | S | 108.6 | 0.85185 | 28.8732 | - | - | 8.1 | 7 | 8.2 | 9.3 | 11.5 | 14.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-NP | W | 115.5 | 0.66667 | 28.8732 | - | - | 8.4 | 7 | 6.7 | 6 | 5.5 | 5.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CRM-FTN/LWN | S | 76 | 1 | 112.2651 | - | - | 12.6 | 16.4 | 18.2 | 19.9 | 21.5 | 23.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CRM-FTN/LWN | W | 96.5 | 0.8 | 112.2651 | - | - | 6 | 4.2 | 4.2 | 4.1 | 3.9 | 3.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN1 | S | 109 | 0.91176 | 39.2799 | - | - | 3.4 | 5.1 | 5.9 | 6.5 | 7.4 | 8.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN1 | W | 116 | 0.46154 | 39.2799 | - | - | 5.2 | 5.8 | 5.8 | 6 | 6.6 | 7.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-KBH | S | 87.5 | 0.92308 | 19.3205 | - | - | 5.2 | 4.7 | 4.6 | 4.1 | 4.4 | 5.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HTS-KBH | W | 87.5 | 0.66667 | 19.3205 | - | - | 1.5 | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN2 | S | 128 | 0.9 | 39.2799 | - | - | 3 | 4.4 | 5.1 | 5.6 | 6.4 | 7.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-MTN2 | W | 134 | 0.44898 | 39.2799 | - | - | 4.9 | 5.5 | 5.5 | 5.6 | 6.2 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC1 | S | 93.2 | 0.28571 | 33.7818 | - | - | 4.9 | 7 | 6.5 | 6.3 | 6.8 | 8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TSTS-DC1 | W | 104.6 | 0.73563 | 33.7818 | - | - | 8.7 | 10.7 | 10.3 | 9.3 | 8.4 | 7.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-DMA | S | 128 | 0.85542 | 26.6771 | - | - | 8.3 | 11.8 | 13.5 | 15.3 | 17.3 | 19.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
TBTS-DMA | W | 134 | 0.11111 | 26.6771 | - | - | 5.4 | 6.4 | 6.6 | 7.1 | 7.8 | 8.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DVY | S | 128 | 1 | 34.1848 | - | - | 3.2 | 6.1 | 4.5 | 7 | 7.4 | 7.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-DVY | W | 133.7 | 0.99174 | 34.1848 | - | - | 12.1 | 6.3 | 9.8 | 11.9 | 11.9 | 11.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-MGE | S | 128 | 0.66304 | 38.3959 | - | - | 9.2 | 8.7 | 10.3 | 11.5 | 13.7 | 16.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
ERTS-MGE | W | 133.7 | 0.36905 | 38.3959 | - | - | 8.4 | 7.2 | 7.4 | 7.2 | 6.9 | 7.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO1 | S | 56 | 0.5 | 51.2696 | - | - | 0.6 | 0.9 | 1 | 1 | 1.1 | 1.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RBD-STO1 | W | 60 | 0.4375 | 51.2696 | - | - | 1.6 | 2.4 | 2.4 | 2.3 | 2.2 | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | S | 94.9 | 0.82927 | 24.9684 | - | - | 4.1 | 5.7 | 5.2 | 4.8 | 4.8 | 5.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVTS-EB | W | 101.7 | 0.94805 | 24.9684 | - | - | 7.7 | 8.2 | 7.8 | 7.3 | 6.7 | 6.1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## ZSS Aug Sum
Zone Substation | Season | Station N Export Rating (MVA) | Station N-1 Export Rating (MVA) | Station Nameplate Rating (MVA) | Station Power Factor at Minimum Demand | Embedded Generation Capacity (MVA) | Load Transfer Capability (MVA) | Generation Headroom (MVA) | Hours load is < 95% of Minimum Demand (Hrs) | Actual Minimum Demand (MVA) | 50% POE |  |  |  |  | % 50% POE load below N-1 Export Rating | 50% POE
[11 empty] | Forecast Minimum Demand (MVA) | [5 empty] | Energy at Risk (MWh) |  |  |  |  | Expected Energy at Risk (MWh) |  |  |  |  | Hours at Risk (Hrs)
[5 empty] | 2025 | 2025 | 2026 | 2025 | 2025 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
BH | summer | -99 | -66 | 99 | 0.99447 | 11.0737 | 26.5514 | 77.0737 | 1.051 | 7.2129 | 7.5323 | 7.4967 | 7.3658 | 7.3255 | 7.3482 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BH | winter | -99 | -66 | 99 | 0.98378 | 11.0737 | 26.5514 | 77.0737 | 1.5681 | 9.036 | 6.906 | 6.8653 | 6.8953 | 6.9412 | 7.0255 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BR | summer | -60 | -30 | 60 | 0.56618 | 12.7852 | 6.7947 | 42.7852 | 0.056283 | -1.1963 | -1.9155 | -2.4192 | -3.1457 | -4.0006 | -5.0166 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BR | winter | -60 | -30 | 60 | 0.72081 | 12.7852 | 6.7947 | 42.7852 | 3.2171 | 1.3733 | 1.5769 | -1.5886 | -1.7918 | -2.1997 | -2.7449 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BT | summer | -60 | -30 | 60 | 0.84904 | 9.9331 | 6.1304 | 39.9331 | 1.3039 | 1.9451 | 2.0017 | 1.6772 | 1.5403 | -1.6726 | -2.2291 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BT | winter | -60 | -30 | 60 | 0.93002 | 9.9331 | 6.1304 | 39.9331 | 5.8446 | 4.1243 | 3.6472 | 3.2765 | 2.8595 | 2.4064 | 1.9091 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BU | summer | -60 | -30 | 60 | 0.48508 | 11.4779 | 7.1401 | 41.4779 | 0.63325 | -0.85062 | -1.0139 | -1.6869 | -2.3547 | -3.1443 | -4.2042 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BU | winter | -60 | -30 | 60 | 0.82735 | 11.4779 | 7.1401 | 41.4779 | 2.5099 | 1.8689 | 1.191 | 0.82861 | 0.44418 | -0.36401 | -1.1521 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BW | summer | -40.5 | -27 | 40.5 | 0.94323 | 12.6848 | 3.3983 | 39.6848 | 0.00059424 | -1.3522 | -1.9426 | -2.3882 | -2.9945 | -3.6648 | -4.3989 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
BW | winter | -40.5 | -27 | 40.5 | 0.57667 | 12.6848 | 3.3983 | 39.6848 | 1.2901 | 0.79856 | 1.566 | 1.4822 | -1.5305 | -1.6832 | -1.9492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CDA | summer | -53 | -20 | 53 | 0.085577 | 9.2696 | 11.1541 | 29.2696 | 0.75907 | -0.84782 | 1.9121 | 1.9481 | 2.2279 | 1.9749 | 1.9194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CDA | winter | -53 | -20 | 53 | 0.94927 | 9.2696 | 11.1541 | 29.2696 | 3.8072 | 2.3477 | 3.8976 | 5.0578 | 5.1413 | 4.824 | 4.4725 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CFD | summer | -66 | -33 | 66 | 0.94828 | 11.9088 | 10.0847 | 44.9088 | 2.4698 | 8.9457 | 10.3667 | 9.9514 | 9.2885 | 8.4768 | 7.5654 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CFD | winter | -66 | -33 | 66 | 0.89341 | 11.9088 | 10.0847 | 44.9088 | 8.395 | 10.9947 | 10.2378 | 10.514 | 10.4782 | 10.1537 | 9.7382 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CM | summer | -60 | -27 | 60 | 0.90226 | 3.1907 | 4.0896 | 30.1907 | 3.0884 | 4.263 | 2.9395 | 3.1073 | 3.2457 | 3.2853 | 3.3149 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CM | winter | -60 | -27 | 60 | 0.89061 | 3.1907 | 4.0896 | 30.1907 | 7.721 | 4.534 | 1.1811 | 1.3693 | 1.5344 | 1.6112 | 1.7077 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CRM | summer | -99 | -66 | 99 | 0.99542 | 64.3961 | 16.6314 | 130.3961 | 0.030649 | -13.9196 | -18.0252 | -19.9905 | -21.7464 | -23.6127 | -25.859 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
CRM | winter | -99 | -66 | 99 | 0.77277 | 64.3961 | 16.6314 | 130.3961 | 0.42121 | -7.0943 | -1.4115 | -1.6589 | -2.1792 | -3.1216 | -4.3514 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DC | summer | -84 | -54 | 84 | 0.28913 | 33.7818 | 19.6314 | 87.7818 | 0.7624 | 4.8886 | 7.0958 | 6.6439 | 6.4001 | -6.8983 | -8.2044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DC | winter | -84 | -54 | 84 | 0.71767 | 33.7818 | 19.6314 | 87.7818 | 3.7804 | 8.871 | 11.0378 | 10.5362 | 9.5391 | 8.6348 | 7.7423 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DMA | summer | -66 | -33 | 66 | 0.92747 | 26.6771 | 23.1522 | 59.6771 | 0.46062 | -4.9939 | -6.364 | -7.2801 | -8.2426 | -9.3128 | -10.5008 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DMA | winter | -66 | -33 | 66 | 0.49436 | 26.6771 | 23.1522 | 59.6771 | 0.4742 | -2.9022 | -3.8302 | -4.1717 | -4.6949 | -5.2892 | -5.9217 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DN | summer | -104 | -66 | 104 | 0.53894 | 36.5567 | 18.5049 | 102.5567 | 0.48898 | -3.7154 | 7.111 | -7.1731 | -7.1186 | -7.2654 | -8.0852 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DN | winter | -104 | -66 | 104 | 0.90261 | 36.5567 | 18.5049 | 102.5567 | 2.6125 | 6.6038 | 9.6202 | 9.8151 | 9.1654 | 8.3802 | 7.689 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DSH | summer | -99 | -66 | 99 | 0.92252 | 11.7446 | 21.9935 | 77.7446 | 2.4965 | 6.5095 | 7.7216 | 8.4008 | 9.2895 | 9.4418 | 9.3665 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DSH | winter | -99 | -66 | 99 | 0.99433 | 11.7446 | 21.9935 | 77.7446 | 3.1849 | 19.619 | 7.8033 | 8.9331 | 9.5172 | 9.5845 | 9.5746 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DVY | summer | -99 | -66 | 99 | 0.54368 | 34.1848 | 11.9272 | 100.1848 | 0.68056 | -1.715 | -6.1886 | -4.6543 | 7.1689 | 7.543 | 7.2228 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DVY | winter | -99 | -66 | 99 | 0.98819 | 34.1848 | 11.9272 | 100.1848 | 3.1747 | 5.0918 | -4.6684 | 6.3462 | 9.8955 | 10.1779 | 10.0681 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EB | summer | -93 | -60 | 93 | 0.83994 | 24.9684 | 15.4184 | 84.9684 | 1.0432 | 4.0493 | 5.5632 | 5.0408 | 4.6824 | -4.6291 | -4.9484 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EB | winter | -93 | -60 | 93 | 0.94584 | 24.9684 | 15.4184 | 84.9684 | 5.9368 | 7.7126 | 8.2334 | 7.7825 | 7.2691 | 6.6234 | 5.9907 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EL | summer | -60 | -27 | 60 | 0.93687 | 7.7984 | 6.3642 | 34.7984 | 2.5861 | 4.2567 | 5.4606 | 5.2376 | 5.3782 | 5.3869 | 4.9008 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EL | winter | -60 | -27 | 60 | 0.93667 | 7.7984 | 6.3642 | 34.7984 | 13.6 | 6.2602 | 6.2139 | 6.45 | 6.8271 | 6.8738 | 6.5811 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EM | summer | -66 | -33 | 54 | 0.70195 | 14.1147 | 8.9538 | 47.1147 | 1.7463 | 4.2525 | 3.3483 | 2.5857 | 1.6678 | 0.77987 | -0.68622 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EM | winter | -66 | -33 | 54 | 0.86661 | 14.1147 | 8.9538 | 47.1147 | 8.7606 | 6.3571 | 5.6802 | 5.0915 | 4.423 | 3.8635 | 3.1488 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EW | summer | -60 | -30 | 60 | 0.72851 | 4.6943 | 3.826 | 34.6943 | 2.113 | 6.7275 | 6.4752 | 6.6113 | 6.742 | 6.7002 | 6.4922 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
EW | winter | -60 | -30 | 60 | 0.76704 | 4.6943 | 3.826 | 34.6943 | 6.2224 | 6.5875 | 6.6349 | 6.8243 | 6.9644 | 7.0759 | 7.1779 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FSH | summer | -93 | -60 | 93 | 0.40635 | 40.9888 | 20.3609 | 100.9888 | 0.041232 | -3.7842 | -5.0401 | -5.684 | -6.861 | -8.4065 | -10.4516 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FSH | winter | -93 | -60 | 93 | 0.66811 | 40.9888 | 20.3609 | 100.9888 | 1.1358 | 4.5759 | 5.3102 | 5.0124 | 4.8733 | -5.0045 | -5.6151 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTN | summer | -66 | -33 | 66 | 0.40322 | 22.2942 | 18.5976 | 55.2942 | 0.75648 | 3.5125 | 6.9608 | 6.8768 | 6.832 | -6.8381 | -7.1418 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FTN | winter | -66 | -33 | 66 | 0.83485 | 22.2942 | 18.5976 | 55.2942 | 6.0599 | 7.0299 | 7.8019 | 7.8281 | 7.5137 | 7.1187 | 6.8918 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GW | summer | -84 | -54 | 84 | 0.98466 | 30.4591 | 19.7027 | 84.4591 | 0.96323 | 2.4398 | 3.3683 | 2.7505 | 2.2982 | 1.7254 | -2.1446 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
GW | winter | -84 | -54 | 84 | 0.99996 | 30.4591 | 19.7027 | 84.4591 | 4.8396 | 7.1766 | 6.8994 | 7.1622 | 6.7056 | 5.8669 | 4.7973 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HGS | summer | -66 | -33 | 66 | 0.98485 | 31.1751 | 14.6135 | 64.1751 | 1.315 | 14.357 | 5 | -5.17 | -5.22 | -5.3 | -5.43 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HGS | winter | -66 | -33 | 66 | 0.97862 | 31.1751 | 14.6135 | 64.1751 | 1.9124 | 11.099 | 5 | -5.17 | -5.22 | -5.3 | -5.43 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HT | summer | -84 | -54 | 84 | 0.87084 | 15.7623 | 26.8666 | 69.7623 | 1.4796 | 2.3778 | 3.2457 | 5.9478 | 9.9893 | 9.28 | 8.3716 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
HT | winter | -84 | -54 | 84 | 0.98935 | 15.7623 | 26.8666 | 69.7623 | 6.536 | 7.4331 | 3.9791 | 6.6053 | 8.3915 | 8.3616 | 8.6712 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K | summer | -60 | -30 | 60 | 0.9995 | 12.4823 | 7.127 | 42.4823 | 2.584 | 6.6764 | 10.8255 | 10.7124 | 10.3993 | 10.12 | 9.7988 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
K | winter | -60 | -30 | 60 | 0.99943 | 12.4823 | 7.127 | 42.4823 | 10.2638 | 7.1209 | 11.0875 | 11.1441 | 11.1583 | 11.1228 | 10.9895 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KBH | summer | -33 | 0 | 33 | 0.94527 | 19.3205 | 33.8719 | 19.3205 | 0.68257 | -5.1144 | -4.623 | -4.5957 | -4.0048 | -4.2619 | -5.0123 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
KBH | winter | -33 | 0 | 33 | 0.76829 | 19.3205 | 33.8719 | 19.3205 | 0.15904 | -3.2477 | -2.1201 | 1.871 | 1.9221 | 1.8838 | -1.9038 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LD | summer | -93 | -60 | 93 | 0.99226 | 34.2166 | 23.8495 | 94.2166 | 0.02918 | -3.5185 | -2.7485 | -3.7195 | -4.1678 | -5.2718 | -7.2069 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LD | winter | -93 | -60 | 93 | 0.50714 | 34.2166 | 23.8495 | 94.2166 | 1.4389 | 1.9425 | 1.9588 | 2.0247 | 1.7977 | 1.2081 | -1.3985 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LWN | summer | -66 | -33 | 66 | 0.95569 | 25.5749 | 26.5994 | 58.5749 | 0.67964 | -4.9287 | -6.28 | -7.383 | -8.4973 | -9.8172 | -11.3459 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
LWN | winter | -66 | -33 | 66 | 0.78389 | 25.5749 | 26.5994 | 58.5749 | 0.70778 | -2.6391 | -3.2573 | -3.7462 | -4.3698 | -5.1239 | -6.0437 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
M | summer | -87 | -54 | 87 | 0.28064 | 15.1827 | 5.21 | 69.1827 | 0.99355 | 1.6574 | 2.3008 | 2.2786 | 2.2726 | -2.2876 | -2.6956 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
M | winter | -87 | -54 | 87 | 0.97408 | 15.1827 | 5.21 | 69.1827 | 3.2942 | 3.7253 | 3.5697 | 3.9386 | 3.8998 | 3.4811 | 3.015 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MC | summer | -87 | -54 | 87 | 0.99976 | 22.935 | 15.1224 | 76.935 | 0.077106 | -2.8919 | -6.6346 | -6.4466 | -5.8354 | -6.6346 | -7.7287 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MC | winter | -87 | -54 | 87 | 0.99467 | 22.935 | 15.1224 | 76.935 | 2.3052 | 3.4351 | 2.5703 | 3.4906 | 3.4621 | 3.023 | 2.6456 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MGE | summer | -99 | -66 | 99 | 0.39584 | 38.3959 | 20.1141 | 104.3959 | 0.63074 | -6.5653 | -5.9259 | -6.7386 | -7.4831 | -8.6341 | -9.8478 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MGE | winter | -99 | -66 | 99 | 0.3448 | 38.3959 | 20.1141 | 104.3959 | 2.4588 | 5.9967 | 5.2285 | 5.2906 | 5.2651 | -5.2135 | -5.4261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MR | summer | -66 | -33 | 66 | 0.64103 | 18.9022 | 15.3105 | 51.9022 | 1.9988 | 2.1697 | 3.4212 | 3.1994 | -3.2041 | -3.483 | -4.1723 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MR | winter | -66 | -33 | 66 | 0.86001 | 18.9022 | 15.3105 | 51.9022 | 7.3758 | 5.4649 | 3.6945 | 3.463 | 3.2614 | 3.1932 | -3.199 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTN | summer | -66 | -33 | 66 | 0.97612 | 39.2799 | 20.6209 | 72.2799 | 0.38466 | -2.4879 | -4.1262 | -5.4727 | -6.5427 | -7.7431 | -9.9304 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
MTN | winter | -66 | -33 | 66 | 0.64863 | 39.2799 | 20.6209 | 72.2799 | 1.3738 | 3.1411 | 2.9971 | -2.9606 | -3.0424 | -3.6956 | -4.8309 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NB | summer | -66 | -33 | 66 | 0.93839 | 12.93 | 7.5605 | 45.93 | 2.5328 | 6.7591 | 7.5042 | 7.0866 | 6.606 | 5.6227 | 4.7344 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NB | winter | -66 | -33 | 66 | 0.89966 | 12.93 | 7.5605 | 45.93 | 8.2933 | 8.7774 | 8.1746 | 8.3359 | 7.7177 | 7.0315 | 6.3333 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NO | summer | -90 | -60 | 90 | 0.95174 | 35.6278 | 6.3953 | 95.6278 | 2.4935 | 9.8697 | 7.5025 | 7.668 | 7.8729 | 7.8495 | 7.8039 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NO | winter | -90 | -60 | 90 | 0.90631 | 35.6278 | 6.3953 | 95.6278 | 8.6217 | 10.7092 | 7.9277 | 8.332 | 8.5221 | 8.6381 | 8.7809 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NP | summer | -90 | -60 | 90 | 0.99981 | 28.8732 | 20.723 | 88.8732 | 0.30474 | -2.7801 | -2.4233 | -3.9876 | -5.749 | -7.4349 | -9.3746 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NP | winter | -90 | -60 | 90 | 0.86913 | 28.8732 | 20.723 | 88.8732 | 1.6827 | 2.544 | 2.7987 | 1.7614 | 0.93048 | -1.2659 | -2.377 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NW | summer | -99 | -66 | 99 | 0.44326 | 28.1572 | 23.1373 | 94.1572 | 0.54173 | -1.6507 | 4.6924 | -4.5925 | -4.8095 | -5.8993 | -7.6967 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
NW | winter | -99 | -66 | 99 | 0.83757 | 28.1572 | 23.1373 | 94.1572 | 4.0898 | 4.6719 | 6.4289 | 5.8451 | 5.0497 | 4.6245 | -4.6098 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OAK | summer | -99 | -66 | 99 | 0.79018 | 13.094 | 4.3696 | 79.094 | 1.9876 | 7.9641 | 6.7342 | 6.8551 | 7.4761 | 8.099 | 8.0488 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OAK | winter | -99 | -66 | 99 | 0.82106 | 13.094 | 4.3696 | 79.094 | 6.0117 | 7.7899 | 8.1745 | 8.5544 | 9.3448 | 9.8703 | 10.0051 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OE | summer | -60 | -30 | 60 | 0.86486 | 5.2224 | 5.3061 | 35.2224 | 1.1059 | 0.40288 | 1.1045 | 1.35 | 1.9671 | 1.5179 | 1.0876 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OE | winter | -60 | -30 | 60 | 0.99682 | 5.2224 | 5.3061 | 35.2224 | 5.5521 | 1.5426 | 2.4163 | 3.4507 | 3.3212 | 3.0637 | 2.758 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OR | summer | -54 | -27 | 54 | 0.141 | 13.5068 | 9.4637 | 40.5068 | 0.52535 | -1.4316 | -2.1129 | -2.23 | -2.3149 | -2.9085 | -3.7031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
OR | winter | -54 | -27 | 54 | 0.73197 | 13.5068 | 9.4637 | 40.5068 | 2.5911 | 2.7417 | 2.7926 | 2.9763 | 2.7145 | 2.3396 | 2.0393 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RBD | summer | -66 | -33 | 66 | 0.90885 | 23.7711 | 16.6809 | 56.7711 | 0.83302 | -3.3753 | -5.468 | -6.5076 | -7.6085 | -8.7128 | -9.8546 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
RBD | winter | -66 | -33 | 66 | 0.087255 | 23.7711 | 16.6809 | 56.7711 | 0.53459 | 2.1433 | -2.5994 | -2.9915 | -3.4315 | -4.0719 | -4.7688 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SH | summer | -20 | -10 | 20 | 0.34863 | 2.5405 | 0 | 12.5405 | 1.3795 | 0.34451 | 0.46325 | 0.43417 | -0.42426 | -0.46325 | -0.59203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SH | winter | -20 | -10 | 20 | 0.89129 | 2.5405 | 0 | 12.5405 | 4.3471 | 0.63507 | 0.58412 | 0.5374 | 0.49204 | 0.45177 | 0.43174 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SR | summer | -54 | -27 | 54 | 0.87858 | 11.1746 | 11.4004 | 38.1746 | 1.0387 | 2.062 | 1.9633 | 1.8159 | -1.869 | -2.2381 | -2.8829 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SR | winter | -54 | -27 | 54 | 0.87056 | 11.1746 | 11.4004 | 38.1746 | 4.6601 | 4.466 | 2.9156 | 2.587 | 2.2509 | 1.9953 | 1.8318 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SS | summer | -66 | -33 | 66 | 0.98711 | 30.1479 | 19.8961 | 63.1479 | 1.8495 | -4.3992 | -2.5146 | -2.7247 | -2.5756 | -3.5618 | -4.5133 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SS | winter | -66 | -33 | 66 | 0.909 | 30.1479 | 19.8961 | 63.1479 | 1.7939 | 3.612 | 2.0008 | 2.6314 | 2.4318 | 1.8285 | 1.3789 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STO | summer | -66 | -33 | 66 | 0.96378 | 27.4985 | 13.2604 | 60.4985 | 0.24529 | -1.4491 | -2.6872 | -3.0392 | -3.3204 | -4.0795 | -4.8518 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
STO | winter | -66 | -33 | 66 | 0.57875 | 27.4985 | 13.2604 | 60.4985 | 0.71569 | 1.2653 | 1.9854 | 1.974 | 1.8613 | -1.801 | -1.8613 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SV | summer | -66 | -33 | 66 | 0.95391 | 15.2168 | 26.8536 | 48.2168 | 1.9918 | 8.106 | 7.2664 | 7.3939 | 7.741 | 7.306 | 6.842 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SV | winter | -66 | -33 | 66 | 0.97024 | 15.2168 | 26.8536 | 48.2168 | 6.6166 | 8.6987 | 5.2912 | 6.045 | 6.4579 | 6.6343 | 6.5271 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVW | summer | -66 | -33 | 66 | 0.99676 | 29.6561 | 26.8536 | 62.6561 | 2.8682 | 8.8264 | 7.7636 | 8.1264 | 8.7154 | 8.5743 | 8.3302 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
SVW | winter | -66 | -33 | 66 | 0.97132 | 29.6561 | 26.8536 | 62.6561 | 5.8022 | 10.5223 | 10.5231 | 11.2798 | 11.6312 | 11.7678 | 11.8267 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WD | summer | -87 | -54 | 87 | 0.97243 | 8.175 | 4.7746 | 62.175 | 2.1484 | 6.4893 | 8.0104 | 7.7021 | 7.318 | 6.923 | 6.5504 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
WD | winter | -87 | -54 | 87 | 0.91811 | 8.175 | 4.7746 | 62.175 | 9.8047 | 9.1227 | 9.4522 | 9.2667 | 8.9628 | 8.6505 | 8.3355 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Note on G1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Lee Conrad, Angelo to add once Max Demand Template EG is filled