## Master Sheet
UE Proj Number | Project Number | Suburb | Voltage at PCC | Generator Technology | Generator Brand | Generator Model | Total Generation (kVA) | Size of Relevant Transformer | Protection and Control Systems | Secondary/Central Protection Relay (Yes/No) | Voltage Control and Reactive Power Capability | Export Control at PCC (Yes/No) | SLD of connection arrangment
91 | 1 | Doncaster | LV | Inverter - Microturbine | Turbec Spa | 1 x Turbec T100 | 100 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
105 | 2 | Hallam | LV | Inverter - Solar | ABB | 4 x PVI-10.0-TL-OUTD-AU 2 x PVI-12.5-TL-OUTD-AU | 65 | 300 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
107 | 3 | Boneo | LV | Synchronous Generator | Caterpillar | 2 x Engine C32 Frame 1424 | 2250 | 1500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
116 | 4 | Scoresby | LV | Inverter - Solar | SMA | 3 x STP15000TL | 45 | 1500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
124 | 5 | Safety Beach | LV | Inverter - Solar | PowerOne | 3 x TRIO-27.6-TL-OUTD | 82.8 | 100 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
127 | 6 | Caulfield South | LV | Synchronous Generator | TEDOM | 1 x TS Micro T30 | 30 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
128 | 7 | Frankston | LV | Synchronous Generator | Caterpillar | 1 x SR4 Frame 447 Arrangement 1938725 | 187 | 1500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
130 | 8 | Clayton | LV | Inverter - Solar | Fronius | 1 x Agilo 100.0-3 | 100 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
132 | 9 | Baxter | LV | Inverter - Solar | SMA | 3 x STP20000TL | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
135 | 10 | Frankston | LV | Synchronous Generator | Caterpillar | 2 x 3512B 512DR7W Arrangement 252-3810 Frame 1447 | 3000 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
137 | 12 | Clayton | LV | Synchronous Generator Inverter - Solar | ABB Cummins | 3 x TRIO-27.6-TL-OUTD 1 x C1100D5 | 1082.8 | 300 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
138 | 13 | Dandenong South | LV | Inverter - Solar | Fronius | 3 x SYMO 15.0 3M 3 x SYMO 10.0 3M | 75 | 100 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
141 | 14 | Nunawading | LV | Inverter - Solar | ABB | 2 x TRIO-27.6-TL-OUTD 3 x PVI-12.5-TL-OUTD | 92.7 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
142 | 15 | Seaford | LV | Inverter - Solar | SunGrow | 4 x SG10KTL | 40 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
143 | 16 | Braeside | LV | Inverter - Solar | SMA | 4 x STP15000TL | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
145 | 17 | Baxter | LV | Inverter - Solar | SMA | 3 x STP20000TL | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
147 | 18 | Clayton | LV | Synchronous Generator | TEDOM | 1 x TS Micro T30 | 30 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
148 | 19 | Somerville | LV | Inverter - Solar | ABB | 3 x PVI-12.5-TL-OUTD | 37.5 | 200 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
149 | 20 | Nunawading | LV | Inverter - Solar | SMA | 2 x STP25000TL | 50 | 2000 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
150 | 21 | Templestowe | LV | Inverter - Solar | ABB | 3 x TRIO-27.6-TL-OUTD | 82.8 | 750 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
151 | 22 | Cheltenham | LV | Inverter - Solar | Zeversolar | 4 x Eversol TLC15k | 60 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
154 | 23 | Carrum Downs | LV | Inverter - Solar | Enphase | 120 x M215-60-230-S22 70 x M250-60-230-S22 | 43.3 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
157 | 24 | Mulgrave | LV | Inverter - Solar | SMA | 4 x STP15000TL 3 x STP20000TL | 120 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
160 | 25 | Malvern | LV | Inverter - Solar | SMA | 2 x STP25000TL-30 | 50 | 1000 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
161 | 26 | Keysborough | LV | Inverter - Solar | SunGrow | 1 x SG30KTL 1 x SG20KTL | 50 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
162 | 27 | Moorabbin Airport | LV | Inverter - Solar | SolarEdge | 7 x SE 17k | 119 | 1500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
163 | 28 | Clayton | HV | Inverter - Solar | Enphase | 255 x M250 | 63.75 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
165 | 29 | Dandenong South | LV | Inverter - Solar | Fronius | 8 x SYMO 20.0 3M 15 x SYMO15.0 3M 1 x SYMO 8.2 3M | 213.2 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
167 | 30 | Hampton Park | LV | Inverter - Solar | Fronius | 3 x SYMO 20.0 3M 1 x SYMO 15.0 3M | 75 | 750 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
168 | 31 | Hampton Park | LV | Inverter - Solar | Fronius | 3 x SYMO 20.0 3M | 60 | 1000 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
169 | 32 | Dandenong South | LV | Inverter - Solar | SMA | 3 x STP25000TL | 75 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
170 | 33 | Dandenong South | LV | Inverter - Solar | SMA | 2 x STP25000TL | 50 | 315 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
173 | 34 | Braeside | LV | Inverter - Solar | ABB | 2 x TRIO 27.6-OUTD | 55.2 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
175 | 35 | Malvern | LV | Inverter - Solar | Schneider | 2 x Conext CL 25000E | 50 | 1500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
177 | 36 | Dandenong South | LV | Inverter - Solar | SMA | 4 x Tripower 25000TL | 100 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
178 | 37 | Endeavour Hills | LV | Inverter - Solar | Fronius | 3 x SYMO 17.5-3-M | 52.5 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
179 | 38 | Carrum Downs | LV | Inverter - Solar | SMA | 2 x STP25000TL | 50 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
182 | 39 | Mount Waverly | LV | Inverter - Solar | SolarEdge | 4 x SE16K-AUS | 64 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
184 | 40 | Dingley | LV | Inverter - Solar | SMA | 4 x STP 25000TL | 100 | 1000 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
195 | 41 | Dandenong South | HV | Inverter - Solar | SMA | 15 x STP60-10 | 900 | HV Customer | Type 2 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
219 | 42 | Black Rock | LV | Inverter - Solar | Fronius | 1 x ECO 25.0-3-S 1 x SYMO 20.0-3-M | 45 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
230 | 43 | Cheltenham | LV | Inverter - Solar | Fronius | 1 x SYMO 15.0.3-M 8 x ECO 27.0-3-S | 231 | 1000 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
245 | 44 | Doncaster | LV | Inverter - Solar | Fronius | 10 x ECO 27.0-3-S | 270 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
255 | 45 | Keysborough | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 1 x SYMO 20.0-3-M | 47 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
256 | 46 | Noble Park | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 1 x SYMO 20.0-3-M | 47 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
259 | 47 | Mentone | LV | Inverter - Solar | SolarEdge | 1 x SE27.6K 1 x SE15K | 42.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
264 | 48 | Braeside | LV | Inverter - Solar | ABB | 3 x TRIO-27.6-TL-OUTD-400 | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
266 | 49 | Frankston | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0.3-M | 80 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
270 | 50 | Springvale | LV | Inverter - Solar | Enphase | 157 x S270 Microinverters | 42.39 | 300 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
271 | 51 | Dandenong South | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x SYMO 20.0-3-M | 74 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
272 | 52 | Dandenong South | LV | Inverter - Solar | Fronius | 4 x ECO 27.0-3-S 1 x SYMO 10.0-3-M | 118 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
275 | 53 | Elsternwick | LV | Inverter - Solar | Fronius | 3 x SYMO 20.0.3-M 1 x SYMO 15.0.3-M 1 x SYMO 10.0.3-M 1 x SYMO 8.2.3-M | 93.2 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
279 | 54 | Mornington | LV | Inverter - Solar | Fronius | 2 x ECO 25.0-3-S | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
280 | 55 | Dandenong South | LV | Inverter - Solar | ABB | 3 x TRIO 27.6-TL-OUTD | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
281 | 56 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | 1 x SPS 30KTL 1 x SPS 20LTL-B | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
283 | 57 | Dandenong South | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S | 54 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
284 | 58 | Sandringham | LV | Inverter - Solar | SMA | 3 x STP 25000TL 1 x STP 20000TL | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
285 | 59 | Beaumaris | LV | Inverter - Solar | SMA | 1 x STP 25000TL 1 x STP 20000TL | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
290 | 60 | Clayton | HV | Inverter - Solar | SMA | 4 x STP25000TL 5 x STP20000TL 2 x STP15000TL | 230 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
291 | 61 | Hallam | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
293 | 62 | Braeside | LV | Inverter - Solar | Goodwe | 5 x GW20K-DT | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
294 | 63 | Dandenong South | LV | Inverter - Solar | SMA | 2 x STP25000TL | 50 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
295 | 64 | Vermont South | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
296 | 65 | Keysborough | LV | Inverter - Solar | SolarEdge | 2 x SE27.6K | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
297 | 66 | Braeside | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K 1 x SE15K | 97.8 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
298 | 67 | Brighton East | LV | Inverter - Solar | SMA | 2 x STP 25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
301 | 68 | Rowville | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0.3-M | 80 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
302 | 69 | Dingley | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
303 | 70 | Braeside | LV | Inverter - Solar | Solis | 6 x Solis-30K | 180 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
306 | 71 | Seaford | LV | Inverter - Solar | Fronius | 6 x ECO 25.0-3-S | 150 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
308 | 72 | Scoresby | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
309 | 73 | Somerville | LV | Inverter - Solar | Fronius | 6 x ECO 25.0-3-S 1 x SYMO 15.0.3-M | 165 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
310 | 74 | Mordialloc | LV | Inverter - Solar | Fronius | 1 x ECO 25.0-3-S 1 x ECO 27.0-3-S | 52 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
311 | 75 | Nunawading | LV | Inverter - Solar | SMA | 2 x STP 20000TL-30 | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
313 | 76 | Seaford | LV | Inverter - Solar | ABB | 2 x TRIO-27.6-TL-OUTD | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
316 | 77 | Balnarring | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S | 75 | 100 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
317 | 78 | Clayton | LV | Inverter - Solar | Surpass Sun Electric | 4 x SPS30KTL 3 x SPS25KTL-B | 195 | 200 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
318 | 79 | Carrum Downs | LV | Inverter - Solar | Goodwe | 3 x GW20K-DT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
319 | 80 | Scoresby | LV | Inverter - Solar | SolarEdge | 5 x SE27.6K | 138 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
320 | 81 | Scoresby | LV | Inverter - Solar | SolarEdge | 6 x SE27.6K | 165.6 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
321 | 82 | Scoresby | LV | Inverter - Solar | SolarEdge | 5 x SE27.6K | 138 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
322 | 83 | Braeside | LV | Inverter - Solar | SMA | 4 x STP25000TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
323 | 84 | Moorabbin | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
324 | 85 | Carrum Down | LV | Inverter - Solar | SMA Fronius | 1 x STP20000TL 1 x STP10000TL 1 x ECO 27.0-3-S | 57 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
327 | 86 | Heatherton | LV | Inverter - Solar | Fronius | 3 x SYMO 20.0-3-M | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
328 | 87 | Springvale | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S 1 x SYMO 12.5-3-M | 87.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
329 | 88 | Cheltenham | LV | Inverter - Solar | Fronius | 2 x ECO 25.0-3-S | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
330 | 89 | Dandenong | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 1 x SYMO 17.5-3-M | 44.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
331 | 90 | Braeside | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 8.2-3-M | 89.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
332 | 91 | Doncaster | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 2 x ECO 25.0-3-S 1 x SYMO 20.0-3-M | 97 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
333 | 92 | Scoresby | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 10.0-3-M | 91 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
335 | 93 | Cheltenham | LV | Inverter - Solar | SMA | 8 x STP 25000TL-30 | 200 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
337 | 94 | Bentleigh | LV | Inverter - Solar | SMA | 3 x STP 20000TL-30 | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
338 | 95 | Hallam | LV | Inverter - Solar | Fronius | 2 x SYMO 20.0-3-M | 40 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
340 | 96 | Carrum Downs | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0-3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
341 | 97 | Carrum Downs | LV | Inverter - Solar | ABB | 3 x TRIO-27.6-TL-OUTD 1 x TRIO-20.0-TL-OUTD | 102.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
343 | 98 | Carrum Downs | LV | Inverter - Solar | ABB | 3 x TRIO-20.0-TL-OUTD | 60 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
345 | 99 | Braeside | LV | Inverter - Solar | SolarEdge | 3 x SE25K | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
349 | 100 | Carrum Downs | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S | 75 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
350 | 101 | Clayton South | LV | Inverter - Solar | SolarEdge | 10 x SE27.6K 5 x SE25k | 401 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
352 | 102 | Noble Park North | LV | Inverter - Solar | SolarEdge | 7 x SE27.6K | 193.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
354 | 103 | Vermont | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
355 | 104 | Brighton | LV | Inverter - Solar | SolarEdge | 1 x SE27.6K 2 x SE25K 1 x SE17K | 94.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
356 | 105 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | 1 x SPS 30KTL 3 x SPS 20KTL-B | 90 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
358 | 106 | Noble Park North | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
361 | 107 | Scoresby | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S 1 x SYMO 20.0-3 M | 95 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
364 | 108 | Brighton | LV | Synchronous Generator | Cummins | 1 x C300 D5 | 300 | 300 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
365 | 109 | Hallam | LV | Inverter - Solar | SolarEdge | 2 x SE27.6K | 55.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
366 | 110 | Dandenong South | LV | Inverter - Solar | Fronius | 6 x 6 x ECO 27.0-3-S | 162 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
369 | 111 | Mount Martha | LV | Inverter - Solar | Fronius | 2 x ECO 25.0-3-S 1 x SYMO 17.5-3-S | 67.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
370 | 112 | Dandenong South | LV | Inverter - Solar | Goodwe | 2 x GW50K-MT | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
371 | 113 | Dandenong | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0 3-M | 80 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
372 | 114 | Dandenong | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0-3-M | 80 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
376 | 115 | Carrum Downs | LV | Inverter - Solar | Goodwe | 3 x GW20K-DT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
379 | 116 | Dandenong South | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 5.0-3-M | 86 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
380 | 117 | Moorooduc | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0-3-M | 80 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
383 | 118 | Dandenong South | LV | Inverter - Solar | Solis | 6 x Solis-30K 1 x Solis-15K | 214.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
387 | 119 | Braeside | LV | Inverter - Solar | Fronius | 2 x SYMO 20.0-3-M | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
390 | 120 | Pearcedale | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-M 1 x SYMO 20.0-3-M 12 x ECO 27.0-3-M 1 x SYMO 17.5-3-M | 436.5 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
391 | 121 | Scoresby | LV | Inverter - Solar | Fronius | 10 x ECO 25.0-3-S | 250 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
393 | 122 | Noble Park | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
394 | 123 | Mornington | LV | Inverter - Solar | ABB | 3 x TRIO-27.6-TL-OUTD | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
396 | 124 | Dandenong South | LV | Inverter - Solar | ABB | 3 x TRIO 27.6-TL-OUTD | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
397 | 125 | Dandenong South | LV | Inverter - Solar | SMA | 1 x STP-50-40 | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
398 | 126 | Dandenong | LV | Inverter - Solar | SolarEdge | 4 x SE25K | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
400 | 127 | Rosebud | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
401 | 128 | Mornington | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
402 | 129 | Hastings | LV | Inverter - Solar | SolarEdge | 1 x SE27.6K 1 x SE15K | 42.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
405 | 130 | Hampton Park | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
410 | 131 | Clayton | LV | Inverter - Solar | Fronius | 2 x SYMO 20.0-3-M 1 x SYMO 15.0-3-M | 55 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
413 | 132 | Dandenong | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 5.0-3-M | 86 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
414 | 133 | Braeside | LV | Inverter - Solar | SolarEdge | 2 x SE25K | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
416 | 134 | Heatherton | LV | Inverter - Solar | SMA | 2 x STP 50-40 | 100 | 1054 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
417 | 135 | Keysborough | LV | Inverter - Solar | Fronius | 4 x SYmo 20.0-3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
418 | 136 | Heatherton | LV | Inverter - Solar | SMA | 2 x STP 50-40 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
419 | 137 | Dandenong | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 7.0 | 88 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
420 | 138 | Dandenong South | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S 1 x SYMO 20.0-3-M | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
421 | 139 | Dandenong South | LV | Inverter - Solar | Huawei | 34 x SUN2000 33KTL | 1020 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
423 | 140 | Boneo | LV | Synchronous Generator | Aggreko G3+ | 1 x Stamford PE734C Winding 312 | 1030 | 1000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
423 | 141 | Dromana | LV | Synchronous Generator | Aggreko G3+ | 2 x Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
423 | 142 | Boneo | LV | Synchronous Generator | Aggreko G3+ | 2 x Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
423 | 143 | Rye | LV | Synchronous Generator | Aggreko G3+ | 2 x Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
423 | 144 | Dromana | LV | Synchronous Generator | Aggreko G3+ | 2 x Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
423 | 145 | Boneo | LV | Synchronous Generator | Aggreko G3+ | 2 x Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
426 | 146 | Cheltenham | LV | Synchronous Generator | Cummins | 1 x C550D5 | 550 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
427 | 147 | Mulgrave | LV | Inverter - Solar | SMA | 2 x STP 50-40 | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
428 | 148 | Cheltenham | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S | 54 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
430 | 149 | Keysborough | LV | Inverter - Solar | SMA | 4 x STP60000TL | 240 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
431 | 150 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | 2 x SPS30KTL 2 x SPS20KTL-B | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
435 | 151 | Dandenong | LV | Inverter - Solar | SolarEdge | 3 x SE25K | 75 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
437 | 152 | Parcedale | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 7.0 | 88 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
440 | 153 | Carrum Downs | LV | Inverter - Solar | ABB | 2 x TRIO-27.5 2 x TRIO-20.0 | 95.2 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
441 | 154 | Glen Waverley | HV | Inverter - Solar | SMA | 5 x STP CORE1 50-40 | 250 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
442 | 155 | Mulgrave | LV | Inverter - Solar | Fronius | 8 x ECO 27.0-3-S | 216 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
443 | 156 | Clayton | LV | Inverter - Solar | SMA | 1 x STP 25000TL-30 1 x STP 20000TL-30 1 x STP 10000TL-20 | 55 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
444 | 157 | Mordialloc | LV | Inverter - Solar | Fronius | 2 x ECO25.0-3-S | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
446 | 158 | Hallam | LV | Inverter - Solar | ABB | 2 x TRIO-27.6-TL-OUTD 2 x TRIO-20.0-TL-OUTD | 95.2 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
447 | 159 | Box Hill | LV | Inverter - Solar | Fronius | 3 x SYMO 20.0-3-M | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
449 | 160 | Oakleigh South | LV | Inverter - Solar | Delta | 3 x M30A | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
450 | 161 | Ashwood | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0-3-M 1 x SYMO 15.0-3-M | 95 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
451 | 162 | Dandenong South | LV | Inverter - Solar | Fronius Diehl | 1 x ECO 25.0-3-S 3 x 22000 TL | 87.1 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
451B | 163 | Dandenong South | LV | Inverter - Solar | Fronius Diehl | 1 x ECO 20.0-3-S 1 x 22000 TL 1 x 13000 TL | 55 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
452 | 164 | Carrum Downs | LV | Inverter - Solar | Surpass Sun Electric | 2 x SPS30KTL 2 x SPS20KTL-B | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
454 | 165 | Braeside | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
455 | 166 | Red Hill | LV | Inverter - Solar | Fronius | 3 x ECO 27.0.3-S 1 x SYMO 15 | 96 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
457 | 167 | Rosebud | LV | Inverter - Solar | SolarEdge | 3 x SE27.6k 1 x SE17k | 99.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
458 | 168 | Hastings | LV | Inverter - Solar | Fronius | 3 x ECO25.0-3-S | 75 | 50 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
463 | 169 | Braeside | LV | Inverter - Solar | SMA | 4 x STP25000TL-30 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
464 | 170 | Dandenong | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0 3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
465 | 171 | Mulgrave | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0 3-M | 80 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
466 | 172 | Rosebud | LV | Inverter - Solar | SolarEdge | 1 x SE82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
467 | 173 | Dandenong | LV | Inverter - Solar | Fronius | 9 x ECO 27.0-3-S 1 x SYMO 12.5-3-M | 255.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
470 | 174 | Cheltenham | LV | Inverter - Solar | Fronius | 2 x SYMO 20.0-3-M | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
472 | 175 | Mulgrave | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x ECO 25.0-3-S | 79 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
474 | 176 | Heatherton | LV | Inverter - Solar | SMA | 4 x STP25000-TL | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
475 | 177 | Clayton | LV | Inverter - Solar | Fronius | 30 x ECO 27.0-3-S 2 x SYMO 17.5-3-M | 845 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
477 | 178 | Braeside | LV | Inverter - Solar | SMA | 4 x STP25000-TL | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
479 | 179 | Dandenong South | LV | Inverter - Solar | SMA | 4 x STP25000TL-30 | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
480 | 180 | Nunawading | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-5 1 x SYMO 5.0-3-M | 86 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
483 | 181 | Braeside | LV | Inverter - Solar | Fronius | 3 x SYMO20.0-3-M | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
484 | 182 | Frankston | LV | Inverter - Solar | Fronius | 1 x ECO 25.0-3-S 2 x ECO 27.0-3-S 1 x SYMO 20.0-3-M | 99 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
486 | 183 | Dandenong | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
487 | 184 | Noble Park | LV | Inverter - Solar | Fronius | 4 x ECO 27.0-3-S | 108 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
491 | 185 | Mitcham | LV | Inverter - Solar | SMA | 5 x STP-50-40 | 250 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
492 | 186 | Vermont | LV | Inverter - Solar | SMA | 3 x STP25000TL | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
493 | 187 | Dromana | LV | Inverter - Solar | Enphase | 200 x IQ 7 Microinverter | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
494 | 188 | Dandenong South | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x SYMO 7.0-3-M | 88 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
495 | 189 | Box Hill North | LV | Inverter - Solar | Fronius | 2 x ECO 27.0.3-S 1 x SYMO 15 1 x SYMO 10 | 79 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
496 | 190 | Oakleigh | LV | Inverter - Solar | Fronius | 1 x SYMO 10kW 3 x ECO 25kW | 85 | 400 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
499 | 191 | Moorabbin | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0-3-M | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
500 | 192 | Cheltenham | LV | Inverter - Solar | SolarEdge | 2 x SE17.5K 2 x SE27.6K | 89.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
501 | 193 | Cheltenham | LV | Inverter - Solar | SolarEdge | 1 x SE17K 3 x SE27.6K | 99.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
502 | 194 | Clayton North | LV | Inverter - Solar | Fronius | 6 x ECO 27.0-3-S 1 x SYMO 7.0-3-M | 169 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
503 | 195 | Clayton | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-s | 81 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
504 | 196 | Braeside | LV | Inverter - Solar | GoodWe | 2 x GW50K-MT | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
507 | 197 | Blackburn South | LV | Inverter - Solar | SMA | 3 x STP 25000TL-30 1 x STP 15000TL-30 | 90 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
509 | 198 | Oakleigh | LV | Inverter - Solar | SolarEdge | 2 x SE82.8K | 165.6 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
510 | 199 | Oakleigh | LV | Inverter - Solar | SolarEdge | 4 x SE82.8K | 331.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
511 | 200 | Box Hill South | LV | Inverter - Solar | ABB | 1 x PVS-100-TL | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
512 | 201 | Dromana | LV | Inverter - Solar | ABB | 1 x PVS-100-TL | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
513 | 202 | Carrum | LV | Inverter - Solar | ABB | 1 x PVS-100-TL | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
515 | 203 | Wantirna South | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x ECO 25.0-3-S | 79 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
516 | 204 | Hastings | LV | Inverter - Solar | SMA | 3 x STP 25000TL-30 1 x STP 15000TL-30 | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
517 | 205 | Fingal | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
518 | 206 | Rosebud | LV | Inverter - Solar | ABB | 1 x PVS-100-TL | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
519 | 207 | Dandenong South | LV | Inverter - Solar | ABB | 13 x PVS-100-TL | 1300 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
521 | 208 | Hallam | LV | Inverter - Solar | SolarEdge | 4 x SolarEdge SE25K | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
525 | 209 | Rosebud | LV | Inverter - Solar | SolarEdge | 1 x SE25K 1 x SE17K | 42 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
529 | 210 | Braeside | LV | Inverter - Solar | Fronius | 1 x SYMO 20.0-3-M 1 x ECO 27.0-3-M | 47 | 315 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
530 | 211 | Hastings | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
531 | 212 | Mulgrave | LV | Inverter - Solar | Fronius | 2 x ECO 25.0-3-S | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
534 | 213 | Malvern East | LV | Inverter - Solar | SolarEdge | 2 x SE25K | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
535 | 214 | Mount Waverly | LV | Inverter - Solar | Fronius | 6 x ECO 27.0-3-S | 162 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
536 | 215 | Hallam | LV | Inverter - Solar | SolarEdge | 2 x SE25K | 50 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
537 | 216 | Dandenong South | LV | Inverter - Solar | GoodWe | 1 x GW50K-MT | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
540 | 217 | Somerville | LV | Inverter - Solar | SolarEdge | 4 x SE25K | 115 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
541 | 218 | Dandenong South | LV | Inverter - Solar | Fronius SunGrow | 2 x ECO 27.0-3-S 1 x SYMO 8.2-3-M 1 x SG30KT2 | 92.2 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
544 | 219 | Dandenong South | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S SYMO 15.0-3-M | 99.82 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
546 | 220 | Noble Park | LV | Inverter - Solar | SolarEdge | 5 x SE82.8K 2 x SE50K | 514 | 1750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
547 | 221 | Dandenong | LV | Inverter - Solar | Fronius | 7 x ECO 27.0-3 | 189 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
549 | 222 | Dandenong | LV | Inverter - Solar | ABB | 2 x PVS-100-TL | 200 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
551 | 223 | Frankston | LV | Inverter - Solar | SolarEdge | 2 x SE82.8k 1 x SE27.6k | 193.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
553 | 224 | Scoresby | LV | Inverter - Solar | SolarEdge | 2 x SE 17K | 34 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
554 | 225 | Dandenong South | LV | Inverter - Solar | SMA | 4 x STP25000TL-30 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
555 | 226 | Caulfield | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S 1 x SYMO 8.2-3-M | 83.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
557 | 227 | Carrum Downs | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
559 | 228 | Chadstone | LV | Inverter - Solar | SolarEdge | 4 x SE82.8K 1 x SE27.6K | 358.8 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
560 | 229 | Bentleigh | LV | Inverter - Solar | SolarEdge | 3 x SE27.6 | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
561 | 230 | Frankston | LV | Inverter - Solar | SolarEdge | 7 x SE82.8K 2 x SE27.6K | 634.8 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
562 | 231 | Cheltenham | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
563 | 232 | Bentleigh East | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S 1 x ECO 25.0-3-S 4 x SSE SPS 25 KTL-B | 206 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
565 | 233 | Keysborough | LV | Inverter - Solar | GoodWe | 1 x GW50K-MT | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
566 | 234 | Mulgrave | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
569 | 235 | Carrum Downs | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x SYMO 20.0-3-M | 74 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
570 | 236 | Carrum Downs | LV | Inverter - Solar | Fronius | 3 x ECO-27-0-3-S | 81 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
571 | 237 | Chelsea Heights | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
572 | 238 | Clayton | HV | Inverter - Solar | SolarEdge | 5 x SE17K 1 x SE25K 5 x SE27.6K 3 x SE50K 3 x SE82.8K | 646.4 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
573 | 239 | Clayton | LV | Inverter - Solar | SolarEdge | 2 x SE17K 1 x SE50K 4 x SE82.8K | 415.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
574 | 240 | Dandenong South, | LV | Inverter - Solar | SMA | 1 x STP50-40 2 x STP15000TL | 80 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
577 | 241 | Templestowe | LV | Inverter - Solar | SolarEdge | 1 x SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
578 | 242 | Cheltenham | LV | Inverter - Solar | SMA | 2 x STP25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
579 | 243 | Vermont | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S1 | 54 | 300 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
581 | 244 | Tyabb | LV | Inverter - Solar | SolarEdge | 1 x SE82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
582 | 245 | Dandenong South | LV | Inverter - Solar | SMA | 2 x STP25000TL | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
585 | 246 | Scoresby | LV | Inverter - Solar | SolarEdge | 3 x SE82.8K 1 x SE50K 5 x SE27.6K | 436.4 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
587 | 247 | Braeside | HV | Inverter - Solar | Fronius | 10 x ECO 27.0-3-S | 270 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
589 | 248 | Rowville | LV | Inverter - Solar | SolarEdge | 1 x SE27.6K 1 x SE25K | 52.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
593 | 249 | Dandenong South | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
597 | 250 | Carrum Downs | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 1 x ECO 25.0-3-S | 52 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
598 | 251 | Dandenong South | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 1 x SYMO 15.0-3-M | 42 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
599 | 252 | Rosebud | LV | Inverter - Solar | SolarEdge | 1 x SE50K | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
603 | 253 | Burwood | LV | Inverter - Solar | Fronius | 10 x ECO 27.0-3-S 1 x ECO 25.0-3-S 2 x SYMO 20.0-3-M 3 x SYMO 17.5-3-M 1 x SYMO 15.0-3-M 3 x SYMO 10.0-3-M | 432.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
609 | 254 | Carrum Downs | LV | Inverter - Solar | Fronius | 2 x SYMO 27.0-3-S 1 x SYMO 12.5-3-S 1 x SYMO 15.0-3-S | 81.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
610 | 255 | Springvale | LV | Inverter - Solar | Fronius | 1 x SYMO 15.0-3-M 6 x SYMO 20.0-3-M 1 x SYMO 25.0-3-S 2 x SYMO 27.0-3-S | 214 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
613 | 256 | Dandenong | LV | Inverter - Solar | Fronius SMA | 3 x SYMO 20.0-3-M 1 x SYMO 10.0-3-M 1 x STP5000TL-20 | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
614 | 257 | Scoresby | LV | Inverter - Solar | Fronius | 2 x ECO 25.0-3-M 1 x SYMO 10.0-3-M | 60 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
615 | 258 | Moorabbin | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S | 54 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
618 | 259 | Hallam | LV | Inverter - Solar | SolarEdge | 1 x SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
623 | 260 | Frankstone | LV | Inverter - Solar | Fronius | 19 x ECO 27.0-3-S 1 x SYMO 25.0-3-M | 538 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
625 | 261 | Mulgrave | HV | Synchronous Generator Inverter - Solar and Battery | SMA Enphase Co gen | SMA STP 15000TL (PV System) SMA STP 20000TL (PV System) SMA STP 25000TL (PV System) Enphase M250 (PV System) SMA STPS 60 (Battery Storage) Elpower Cleanisland 180kVA (Battery Storage) | 3483.92 | HV Customer | Type 3 and Type 4 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
629 | 262 | Moorooduc | LV | Inverter - Solar | SolarEdge | 1 x SE50K | 50 | 50 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
631 | 263 | Nunawading | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S | 54 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
636 | 264 | Glen Waverly | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x ECO 25.0-3-S | 79 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
638 | 265 | Keysborough | LV | Inverter - Solar | Fronius | 4 x SYMO 20.0-3-M | 80 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
640 | 266 | Mornington | LV | Inverter - Solar | Fronius | 2 x SYMO 20.0-3-M 1 x SYMO 10.0-3-M 1 x ECO 25.0-3-S | 75 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
641 | 267 | Mornington | LV | Inverter - Solar | Fronius | 2 x SYMO 20.0-3-M 1 x SYMO 10.0-3-M | 50 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
645 | 268 | Chelsea | LV | Inverter - Solar | SolarEdge | 1 x SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
646 | 269 | Mount Martha | LV | Inverter - Solar | Fronius | 5 x SYMO 20.0-3-M | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
651 | 270 | Mulgrave | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x SYMO 3.0.3-M | 57 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
653 | 271 | Burwood | LV | Inverter - Solar | Fronius | 1 x SYMO 20.0-3-M 1 x SYMO 17.5-3-M 1 x SYMO 15.0-3-M | 52.5 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
654 | 272 | Mentone | LV | Inverter - Solar | Fronius | 3 x ECO 25.0-3-S 1 x SYMO 17.5-3-M | 92.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
658 | 273 | Clayton | LV | Inverter - Solar | Fronius | 2 x ECO 25.0-3-S 1 x SYMO 17.5-3-M | 67.5 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
659 | 274 | Lower Templestowe | LV | Inverter - Solar | SMA | 2 x STP 50-40 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
660 | 275 | Clayton South | LV | Inverter - Solar | SMA | 2 x STP 50-40 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
662 | 276 | Dandenong South | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S 1 x SYMO 7.0-3-M | 61 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
670 | 277 | Dandenong South | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
681 | 278 | Carrum Downs | LV | Inverter - Solar | SolarEdge | 1 x 82.8K | 82.8 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
682 | 279 | Carrum Downs | LV | Inverter - Solar | Fronius | 3 x ECO 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
698 | 280 | Keysborough | LV | Inverter - Solar | Huawei | 1 x SUN2000-50KTL | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
286 | 281 | Burwood | LV | Inverter - Solar | SolarEdge | 2 x SE27.6k | 55.2 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
305 | 282 | Donvale | LV | Inverter - Solar | Fronius | 14 x ECO 25.0-3-S | 350 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
326 | 283 | Rowville | LV | Inverter - Solar | Solar Edge | 2 x SE25k | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
339 | 284 | Flinders | LV | Inverter - Solar | Enphase Energy | 236 x S270-72-LN-2-AU | 64 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
346 | 285 | Mentone | LV | Inverter - Solar | Zeversolar GoodWe | 2 x Eversol TLC20K 2 x GW25K-DT | 90 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
360 | 286 | Moorabbin | LV | Inverter - Solar | Fronius | 2 x ECO 27.0-3-S | 54 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
362 | 287 | Dandenong South | LV | Inverter - Solar | Fronius | 9 x ECO 25.0-3-S 3 x SYMO 20.0-3-M 1 x SYMO 12.5-3-M | 297.5 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
384 | 288 | Dandenong South | LV | Inverter - Solar | SolarEdge | 3 x SE27.6K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
386 | 289 | Keysborough | LV | Inverter - Solar | SMA | 2 x STP 25000TL-30 | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
395 | 290 | Dandenong | LV | Inverter - Solar | SMA | 2 x STP 25000TL-30 | 50 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
397 | 291 | Dandenong South | LV | Inverter - Solar | SMA | 1 x STP-50-40 | 50 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
407 | 292 | Malvern | LV | Inverter - Solar | Fronius | 1 x ECO 27.0-3-S 2 x SYMO 20.0-3-M 1 x SYMO 17.5-3-M | 84.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
411 | 293 | Dandenong | LV | Inverter - Solar | Fronius | 4 x ECO 25.0-3-S | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
422 | 294 | Dandenong South | LV | Inverter - Solar | SMA | 4 x STP25000-TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
432 | 295 | Blackburn | LV | Inverter - Solar | Solar Edge | 2 x SE17K | 34 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
468 | 296 | Clayton South | LV | Inverter - Solar | Jiangsu GoodWe | 2 x GW50K-MT | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
514 | 297 | Somers | LV | Inverter - Solar | SMA Australia Pty Ltd | 1 X STP15000TL-30 | 15 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No
514 | 297 | Somers | LV | Inverter - Solar | Enphase | 122 X iQ7 | 30.5 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No
693 | 298 | Breaside | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No
695 | 299 | Dandenong South | LV | Inverter - Solar | SMA Australia Pty Ltd | 4 X STP25000TL-30 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No
696 | 300 | Hallam | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 10.0-3-M | 10 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No
696 | 300 | Hallam | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 20.0-3-M | 40 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
697 | 301 | Sommerville | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-50KTL-M0 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
697 | 301 | Sommerville | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-29.9KTL | 29.9 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
698 | 302 | Keysborough | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-50KTL-M0 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
699 | 303 | Brighton | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
700 | 304 | Mornington | LV | Inverter - Solar | SolarEdge Technologies Ltd | 3 X SE27.6K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
702 | 305 | Nunawading | LV | Inverter - Solar | SMA Australia Pty Ltd | 4 X STP25000TL-30 | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
703 | 306 | Highett | LV | Inverter - Solar | Fronius Australia | 1 X 27.0-3-S | 27 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
703 | 306 | Highett | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
704 | 307 | Nunawading | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
706 | 308 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 2 X 25.0-3-S | 50 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
706 | 308 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 20.0-3-M | 40 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
707 | 309 | Brighton East | LV | Inverter - Solar | Fronius Australia | 2 X 25.0-3-S | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
707 | 309 | Brighton East | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 15.0-3-M | 30 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
707 | 309 | Brighton East | LV | Inverter - Solar | Fronius International GmbH | 3 X Symo 20.0-3-M | 60 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
707 | 309 | Brighton East | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 10.0-3-M | 10 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
708 | 310 | Oakleigh | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP 50-40 | 150 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
709 | 311 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 20.0-3-M | 40 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
709 | 311 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 15.0-3-M | 15 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
709 | 311 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 10.0-3-M | 10 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
710 | 312 | Carrum Downs | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
711 | 313 | Carrum Downs | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-50KTL-M0 | 55 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
711 | 313 | Carrum Downs | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-29.9KTL | 29.9 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
712 | 314 | Carrum Downs | LV | Inverter - Solar | Fronius Australia | 1 X 27.0-3-S | 27 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
712 | 314 | Carrum Downs | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
713 | 315 | Mount Waverly | LV | Inverter - Solar | SMA Australia Pty Ltd | 1 X STP 50-40 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
715 | 316 | Safety Beach | LV | Inverter - Solar | Fronius Australia | 3 X 25.0-3-S | 75 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
715 | 316 | Safety Beach | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 15.0-3-M | 15 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
716 | 317 | Mulgrave | LV | Inverter - Solar | Fronius International GmbH | 4 X Symo 20.0-3-M | 80 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
717 | 318 | Noble Park | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 20.0-3-M | 40 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
718 | 319 | Moorabbin | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
719 | 320 | Sommerville | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP 50-40 | 100 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
721 | 321 | Cheltenham | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
723 | 322 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
723 | 322 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 1 X 27.0-3-S | 27 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
725 | 323 | Hallam | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 20.0-3-M | 40 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
726 | 324 | Frankston | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP 50-40 | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
727 | 325 | Heatherton | LV | Inverter - Solar | Fronius International GmbH | 4 X Symo 20.0-3-M | 80 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | 326 | Burwood | LV | Inverter - Solar | Fronius Australia | 10 X 27.0-3-S | 270 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | 326 | Burwood | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | 326 | Burwood | LV | Inverter - Solar | Fronius International GmbH | 4 X Symo 20.0-3-M | 80 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | 326 | Burwood | LV | Inverter - Solar | Fronius International GmbH | 3 X Symo 17.5-3-M | 52.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | 326 | Burwood | LV | Inverter - Solar | Fronius International GmbH | 5 X Symo 10.0-3-M | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
728 | 326 | Burwood | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 15.0-3-M | 15 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
729 | 327 | Mt Waverley | LV | Inverter - Solar | Fronius International GmbH | 2 X Symo 20.0-3-M | 40 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
729 | 327 | Mt Waverley | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 10.0-3-M | 10 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
730 | 328 | Hallam | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
731 | 329 | Box Hill | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
731 | 329 | Box Hill | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 8.2-3-M | 8.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
733 | 330 | Braeside | LV | Inverter - Solar | Fronius Australia | 2 X 25.0-3-S | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
734 | 331 | Caulfield North | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
734 | 331 | Caulfield North | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
734 | 331 | Caulfield North | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 17.5-3-M | 17.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
734 | 331 | Caulfield North | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 15.0-3-M | 15 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
734 | 331 | Caulfield North | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 12.5-3-M | 12.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
735 | 332 | Keysborough | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP25000TL-30 | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
735 | 332 | Keysborough | LV | Inverter - Solar | SMA Australia Pty Ltd | 1 X STP15000TL-30 | 15 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
737 | 333 | Carrum Downs | LV | Inverter - Solar | Fronius Australia | 4 X 25.0-3-S | 100 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
738 | 334 | Carrum Downs | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP 50-40 | 100 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
739 | 335 | Dandenong | LV | Inverter - Solar | Fronius | 1 X CL 36.0 | 36 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
739 | 335 | Dandenong | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 15.0-3-M | 15 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
740 | 336 | Braeside | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
741 | 337 | Bentleigh | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
742 | 338 | Mulgrave | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP20000TL-30 | 40 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
743 | 339 | Carrum Downs | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP25000TL-30 | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
747 | 340 | Notting Hill | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
748 | 341 | Tuerong | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP 50-40 | 100 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
749 | 342 | Doncaster | LV | Inverter - Solar | Fronius Australia | 1 X 27.0-3-S | 27 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
749 | 342 | Doncaster | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
750 | 343 | Dandenong South | LV | Inverter - Solar | Jiangsu GoodWe Power Supply Technology Co Ltd | 1 X GW60K-MT | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
750 | 343 | Dandenong South | LV | Inverter - Solar | Jiangsu GoodWe Power Supply Technology Co Ltd | 1 X GW20K-DT | 20 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
751 | 344 | Hastings | LV | Inverter - Solar | Fronius Australia | 2 X 27.0-3-S | 54 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
752 | 345 | Dandenong South | LV | Inverter - Solar | Sungrow Power Supply Co Ltd | 1 X SG110CX | 110 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
753 | 346 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 4 X Symo 20.0-3-M | 80 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
755 | 347 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
756 | 348 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 4 X Symo 20.0-3-M | 80 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
757 | 349 | Dandenong | LV | Inverter - Solar | SMA Australia Pty Ltd | 7 X STP25000TL-30 | 175 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
757 | 349 | Dandenong | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP20000TL-30 | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
758 | 350 | Braeside | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
758 | 350 | Braeside | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 10.0-3-M | 10 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
759 | 351 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 4 X Symo 15.0-3-M | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
759 | 351 | Dandenong South | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
760 | 352 | Cape Schanck | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 15.0-3-M | 15 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
760 | 352 | Cape Schanck | LV | Inverter - Solar | Fronius Australia | 5 X 25.0-3-S | 125 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
761 | 353 | Cape Schanck | LV | Inverter - Solar | Fronius Australia | 2 X 27.0-3-S | 54 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
761 | 353 | Cape Schanck | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
762 | 354 | Cape Schanck | LV | Inverter - Solar | Fronius International GmbH | 3 X Symo 20.0-3-M | 60 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
762 | 354 | Cape Schanck | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 8.2-3-M | 8.2 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
762 | 354 | Cape Schanck | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 12.5-3-M | 12.5 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
764 | 355 | Blackburn | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-10kTL-M0 | 11 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
764 | 355 | Blackburn | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-50KTL-M0 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
764 | 355 | Blackburn | LV | Inverter - Battery | Sonnen GmbH | 3 X eco 8.2/12 | 7.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
765 | 356 | Somerville | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-29.9KTL | 29.9 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
765 | 356 | Somerville | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-20KTL | 22 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
765 | 356 | Somerville | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-33KTL | 33 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
766 | 357 | Dromana | LV | Inverter - Solar | Samil Power | 1 X Solar Lake 15000TL | 15 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
766 | 357 | Dromana | LV | Inverter - Solar | Samil Power | 1 X Solar River 5200TL | 5.2 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
766 | 357 | Dromana | LV | Inverter - Solar | Samil Power | 2 X SR2K8TLA1 | 5.6 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
766 | 357 | Dromana | LV | Inverter - Solar | Fronius Australia | 1 X 27.0-3-S | 27 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
769 | 358 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
770 | 359 | Braeside | LV | Inverter - Solar | Jiangsu GoodWe Power Supply Technology Co Ltd | 2 X GW30K-MT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
771 | 360 | Braeside | LV | Inverter - Solar | Jiangsu GoodWe Power Supply Technology Co Ltd | 2 X GW30K-MT | 60 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
772 | 361 | Brighton East | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
774 | 362 | Dandenong South | LV | Inverter - Solar | Jiangsu GoodWe Power Supply Technology Co Ltd | 2 X GW29.9K-MT | 59.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
777 | 363 | Notting Hill | LV | Inverter - Solar | Huawei Technologies Co Ltd | 2 X SUN2000-50KTL-M0 | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
778 | 364 | Braeside | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP25000TL-30 | 50 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
780 | 365 | Braeside | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
780 | 365 | Braeside | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
781 | 366 | Braeside | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
781 | 366 | Braeside | LV | Inverter - Solar | Fronius Australia | 1 X 27.0-3-S | 27 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
782 | 367 | Dandenong | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
785 | 368 | Nunawading | LV | Inverter - Solar | SMA | 3 X 6000A-1 | 18 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
785 | 368 | Nunawading | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE10K | 10 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
785 | 368 | Nunawading | LV | Inverter - Solar | SolarEdge Technologies Ltd | 2 X SE27.6K | 55.2 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
787 | 369 | Keysborough | LV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-50KTL-M0 | 55 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
788 | 370 | Frankston | LV | Inverter - Solar | SMA Australia Pty Ltd | 1 X STP15000TL-30 | 15 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
788 | 370 | Frankston | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP25000TL-30 | 75 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
789 | 371 | Moorabbin | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
789 | 371 | Moorabbin | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
790 | 372 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
791 | 373 | Dandenong | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
792 | 374 | Frankston | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE82.8K | 82.8 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
793 | 375 | Dandenong South | LV | Inverter - Solar | Sungrow Power Supply Co Ltd | 1 X SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
794 | 376 | Dandenong South | LV | Inverter - Solar | Sungrow Power Supply Co Ltd | 1 X SG110CX | 110 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
796 | 377 | Red Hill | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
796 | 377 | Red Hill | LV | Inverter - Solar | Fronius Australia | 2 X 27.0-3-S | 54 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
796 | 377 | Red Hill | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 20.0-3-M | 20 | 200 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
800 | 378 | Dandenong South | HV | Inverter - Solar | Huawei Technologies Co Ltd | 1 X SUN2000-50KTL-M0 | 55 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
803 | 379 | Burwood East | LV | Inverter - Solar | SMA Australia Pty Ltd | 4 X STP25000TL-30 | 100 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
804 | 380 | Dandenong | LV | Inverter - Solar | Sungrow Power Supply Co Ltd | 1 X SG110CX | 110 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
805 | 381 | Burwood East | LV | Inverter - Solar | SMA Australia Pty Ltd | 9 X STP25000TL-30 | 225 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
805 | 381 | Burwood East | LV | Inverter - Solar | SMA Australia Pty Ltd | 1 X STP10000TL-20 | 10 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
806 | 382 | Noble Park North | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP25000TL-30 | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
808 | 383 | Nunawading | LV | Inverter - Solar | SMA Australia Pty Ltd | 2 X STP25000TL-30 | 50 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
812 | 384 | Hastings | LV | Inverter - Solar | Fronius Australia | 2 X 27.0-3-S | 54 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
814 | 385 | Glen Waverley | LV | Inverter - Solar | Fronius Australia | 4 X 25.0-3-S | 100 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
815 | 386 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
816 | 387 | Notting Hill | LV | Inverter - Solar | Fronius Australia | 3 X 27.0-3-S | 81 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
817 | 388 | Carrum Downs | LV | Inverter - Solar | Fronius Australia | 3 X 25.0-3-S | 75 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
818 | 389 | Blackburn | LV | Inverter - Solar | Fronius International GmbH | 3 X Symo 20.0-3-M | 60 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
818 | 389 | Blackburn | LV | Inverter - Solar | Fronius International GmbH | 1 X Symo 10.0-3-M | 10 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
820 | 390 | West Somerville | LV | Inverter - Solar | SMA Australia Pty Ltd | 3 X STP25000TL-30 | 75 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
820 | 390 | West Somerville | LV | Inverter - Solar | SMA Australia Pty Ltd | 1 X STP15000TL-30 | 15 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
824 | 391 | Merricks | LV | Inverter - Solar | SolarEdge Technologies Ltd | 1 X SE50K | 50 | 100 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
826 | 392 | Springvale | LV | Inverter - Solar | Sungrow Power Supply Co Ltd | 1 X SG110CX | 110 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
831 | 393 | Box Hill South | LV | Inverter - Solar | Gsmart | 60 X GS500 | 30 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
831 | 393 | Box Hill South | LV | Inverter - Solar | Fronius Australia | 1 X 25.0-3-S | 25 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
833 | 394 | Mulgrave | LV | Inverter - Solar | SolarEdge Technologies Ltd | 3 X SE27.6K | 82.8 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
834 | 395 | Notting Hill | LV | Inverter - Solar | Sungrow Power Supply Co Ltd | 1 X SG110CX | 110 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
835 | 396 | Dandenong South | LV | Inverter - Solar | Fronius Australia | 2 X 27.0-3-S | 54 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
Note on J1: Tnay, Kaisui: More details about the protection types can be found in the worksheet titled "Prot Types"
Note on N1: Tnay, Kaisui: More details about the protection types can be found in the worksheet titled "SLD Types"

## Sheet2
Model | Qty
STP15000TL-30 | 1 | 1 X STP15000TL-30
iQ7 | 122 | 122 X iQ7
27.0-3-S | 3 | 3 X 27.0-3-S
STP25000TL-30 | 4 | 4 X STP25000TL-30
Symo 10.0-3-M | 1 | 1 X Symo 10.0-3-M
Symo 20.0-3-M | 2 | 2 X Symo 20.0-3-M
SUN2000-50KTL-M0 | 1 | 1 X SUN2000-50KTL-M0
SUN2000-29.9KTL | 1 | 1 X SUN2000-29.9KTL
SUN2000-50KTL-M0 | 1 | 1 X SUN2000-50KTL-M0
SE82.8K | 1 | 1 X SE82.8K
SE27.6K | 3 | 3 X SE27.6K
STP25000TL-30 | 4 | 4 X STP25000TL-30
27.0-3-S | 1 | 1 X 27.0-3-S
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
SE82.8K | 1 | 1 X SE82.8K
25.0-3-S | 2 | 2 X 25.0-3-S
Symo 20.0-3-M | 2 | 2 X Symo 20.0-3-M
25.0-3-S | 2 | 2 X 25.0-3-S
Symo 15.0-3-M | 2 | 2 X Symo 15.0-3-M
Symo 20.0-3-M | 3 | 3 X Symo 20.0-3-M
Symo 10.0-3-M | 1 | 1 X Symo 10.0-3-M
STP 50-40 | 3 | 3 X STP 50-40
Symo 20.0-3-M | 2 | 2 X Symo 20.0-3-M
Symo 15.0-3-M | 1 | 1 X Symo 15.0-3-M
Symo 10.0-3-M | 1 | 1 X Symo 10.0-3-M
SE82.8K | 1 | 1 X SE82.8K
SUN2000-50KTL-M0 | 1 | 1 X SUN2000-50KTL-M0
SUN2000-29.9KTL | 1 | 1 X SUN2000-29.9KTL
27.0-3-S | 1 | 1 X 27.0-3-S
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
STP 50-40 | 1 | 1 X STP 50-40
25.0-3-S | 3 | 3 X 25.0-3-S
Symo 15.0-3-M | 1 | 1 X Symo 15.0-3-M
Symo 20.0-3-M | 4 | 4 X Symo 20.0-3-M
Symo 20.0-3-M | 2 | 2 X Symo 20.0-3-M
SE82.8K | 1 | 1 X SE82.8K
STP 50-40 | 2 | 2 X STP 50-40
SE82.8K | 1 | 1 X SE82.8K
25.0-3-S | 1 | 1 X 25.0-3-S
27.0-3-S | 1 | 1 X 27.0-3-S
Symo 20.0-3-M | 2 | 2 X Symo 20.0-3-M
STP 50-40 | 2 | 2 X STP 50-40
Symo 20.0-3-M | 4 | 4 X Symo 20.0-3-M
27.0-3-S | 10 | 10 X 27.0-3-S
25.0-3-S | 1 | 1 X 25.0-3-S
Symo 20.0-3-M | 4 | 4 X Symo 20.0-3-M
Symo 17.5-3-M | 3 | 3 X Symo 17.5-3-M
Symo 10.0-3-M | 5 | 5 X Symo 10.0-3-M
Symo 15.0-3-M | 1 | 1 X Symo 15.0-3-M
Symo 20.0-3-M | 2 | 2 X Symo 20.0-3-M
Symo 10.0-3-M | 1 | 1 X Symo 10.0-3-M
27.0-3-S | 3 | 3 X 27.0-3-S
27.0-3-S | 3 | 3 X 27.0-3-S
Symo 8.2-3-M | 1 | 1 X Symo 8.2-3-M
25.0-3-S | 2 | 2 X 25.0-3-S
25.0-3-S | 1 | 1 X 25.0-3-S
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
Symo 17.5-3-M | 1 | 1 X Symo 17.5-3-M
Symo 15.0-3-M | 1 | 1 X Symo 15.0-3-M
Symo 12.5-3-M | 1 | 1 X Symo 12.5-3-M
STP25000TL-30 | 3 | 3 X STP25000TL-30
STP15000TL-30 | 1 | 1 X STP15000TL-30
25.0-3-S | 4 | 4 X 25.0-3-S
STP 50-40 | 2 | 2 X STP 50-40
CL 36.0 | 1 | 1 X CL 36.0
Symo 15.0-3-M | 1 | 1 X Symo 15.0-3-M
27.0-3-S | 3 | 3 X 27.0-3-S
SE82.8K | 1 | 1 X SE82.8K
STP20000TL-30 | 2 | 2 X STP20000TL-30
STP25000TL-30 | 3 | 3 X STP25000TL-30
27.0-3-S | 3 | 3 X 27.0-3-S
STP 50-40 | 2 | 2 X STP 50-40
27.0-3-S | 1 | 1 X 27.0-3-S
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
GW60K-MT | 1 | 1 X GW60K-MT
GW20K-DT | 1 | 1 X GW20K-DT
27.0-3-S | 2 | 2 X 27.0-3-S
SG110CX | 1 | 1 X SG110CX
Symo 20.0-3-M | 4 | 4 X Symo 20.0-3-M
27.0-3-S | 3 | 3 X 27.0-3-S
Symo 20.0-3-M | 4 | 4 X Symo 20.0-3-M
STP25000TL-30 | 7 | 7 X STP25000TL-30
STP20000TL-30 | 3 | 3 X STP20000TL-30
27.0-3-S | 3 | 3 X 27.0-3-S
Symo 10.0-3-M | 1 | 1 X Symo 10.0-3-M
Symo 15.0-3-M | 4 | 4 X Symo 15.0-3-M
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
Symo 15.0-3-M | 1 | 1 X Symo 15.0-3-M
25.0-3-S | 5 | 5 X 25.0-3-S
27.0-3-S | 2 | 2 X 27.0-3-S
25.0-3-S | 1 | 1 X 25.0-3-S
Symo 20.0-3-M | 3 | 3 X Symo 20.0-3-M
Symo 8.2-3-M | 1 | 1 X Symo 8.2-3-M
Symo 12.5-3-M | 1 | 1 X Symo 12.5-3-M
SUN2000-10kTL-M0 | 1 | 1 X SUN2000-10kTL-M0
SUN2000-50KTL-M0 | 1 | 1 X SUN2000-50KTL-M0
eco 8.2/12 | 3 | 3 X eco 8.2/12
SUN2000-29.9KTL | 1 | 1 X SUN2000-29.9KTL
SUN2000-20KTL | 1 | 1 X SUN2000-20KTL
SUN2000-33KTL | 1 | 1 X SUN2000-33KTL
Solar Lake 15000TL | 1 | 1 X Solar Lake 15000TL
Solar River 5200TL | 1 | 1 X Solar River 5200TL
SR2K8TLA1 | 2 | 2 X SR2K8TLA1
27.0-3-S | 1 | 1 X 27.0-3-S
27.0-3-S | 3 | 3 X 27.0-3-S
GW30K-MT | 2 | 2 X GW30K-MT
GW30K-MT | 2 | 2 X GW30K-MT
SE82.8K | 1 | 1 X SE82.8K
GW29.9K-MT | 2 | 2 X GW29.9K-MT
SUN2000-50KTL-M0 | 2 | 2 X SUN2000-50KTL-M0
STP25000TL-30 | 2 | 2 X STP25000TL-30
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
27.0-3-S | 1 | 1 X 27.0-3-S
SE82.8K | 1 | 1 X SE82.8K
6000A-1 | 3 | 3 X 6000A-1
SE10K | 1 | 1 X SE10K
SE27.6K | 2 | 2 X SE27.6K
SUN2000-50KTL-M0 | 1 | 1 X SUN2000-50KTL-M0
STP15000TL-30 | 1 | 1 X STP15000TL-30
STP25000TL-30 | 3 | 3 X STP25000TL-30
25.0-3-S | 1 | 1 X 25.0-3-S
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
27.0-3-S | 3 | 3 X 27.0-3-S
SE82.8K | 1 | 1 X SE82.8K
SE82.8K | 1 | 1 X SE82.8K
SG110CX | 1 | 1 X SG110CX
SG110CX | 1 | 1 X SG110CX
25.0-3-S | 1 | 1 X 25.0-3-S
27.0-3-S | 2 | 2 X 27.0-3-S
Symo 20.0-3-M | 1 | 1 X Symo 20.0-3-M
SUN2000-50KTL-M0 | 1 | 1 X SUN2000-50KTL-M0
STP25000TL-30 | 4 | 4 X STP25000TL-30
SG110CX | 1 | 1 X SG110CX
STP25000TL-30 | 9 | 9 X STP25000TL-30
STP10000TL-20 | 1 | 1 X STP10000TL-20
STP25000TL-30 | 3 | 3 X STP25000TL-30
STP25000TL-30 | 2 | 2 X STP25000TL-30
27.0-3-S | 2 | 2 X 27.0-3-S
25.0-3-S | 4 | 4 X 25.0-3-S
27.0-3-S | 3 | 3 X 27.0-3-S
27.0-3-S | 3 | 3 X 27.0-3-S
25.0-3-S | 3 | 3 X 25.0-3-S
Symo 20.0-3-M | 3 | 3 X Symo 20.0-3-M
Symo 10.0-3-M | 1 | 1 X Symo 10.0-3-M
STP25000TL-30 | 3 | 3 X STP25000TL-30
STP15000TL-30 | 1 | 1 X STP15000TL-30
SE50K | 1 | 1 X SE50K
SG110CX | 1 | 1 X SG110CX
GS500 | 60 | 60 X GS500
25.0-3-S | 1 | 1 X 25.0-3-S
SE27.6K | 3 | 3 X SE27.6K
SG110CX | 1 | 1 X SG110CX
27.0-3-S | 2 | 2 X 27.0-3-S

## Prot Types
Protection Type | Generator Protection Functions | Central/Secondary Prot Relay Functions | Comments
1 | Over Frequency | No Secondary Protection Relay | Applicable to inverter based installations with total capacity < 100kVA whose application was submitted prior to 1 May 2017
Under Frequency
Over Voltage
Under Voltage
2 | Over Frequency | Over Frequency | Applicable to inverter based installations with total capacity > 100kVA whose application was submitted prior to 1 May 2017
| Under Frequency | Under Frequency
| Over Voltage | Over Voltage
| Under Voltage | Under Voltage
ROCOF
Vector Shift
3 | Over Frequency | Over Frequency | Applicable to all negotiated inverter based installations whose application was submitted after or on 1 May 2017
| Under Frequency | Under Frequency
| Fast Over Voltage | Fast Over Voltage
| Over Voltage | Over Voltage
| Sustained Over Voltage | Sustained Over Voltage
| Under Voltage | Under Voltage
| Soft Export Limit (where applicable) | ROCOF
Vector Shift
Reverse Power (where applicable)
4 | Over Frequency | Over Frequency | Applicable to all non-inverter based installations
| Under Frequency | Under Frequency
| Fast Over Voltage | Fast Over Voltage
| Over Voltage | Over Voltage
| Under Voltage | Under Voltage
| ROCOF | ROCOF
| Vector Shift | Vector Shift
| Reverse Power | Reverse Power (where applicable)
| Synch Check | Synch Check
Current based protection (O/C, E/F)
Negative Sequence Protection
Neutral Voltage Displacement (where possible) - e.g. HV customer not connected to a REFCL enabled feeder