## Master Sheet
UEProjNo | Suburb | Voltage at PCC | Generation Technology | Generator Brand | Generator Model | Total Generation (kVA) | Transformer Size (kVA) | Protection and Control Systems | Secondary/Central Protection Relay (Yes/No) | Voltage Control and Reactive Power Capability | Export Control at PCC (Yes/No) | SLD of connection arrangment
1 | Clayton | HV | Synchronous - Gas | Caterpillar | 3516 | 12000 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
2 | Bangholme | HV | Synchronous - Gas | Deutz | TBG 620V16 | 11760 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
3 | Mount Eliza | LV | Synchronous - Diesel | Cummins | 715DQCC | 894 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
4 | Burwood East | LV | Synchronous - Diesel | Caterpillar | 3412 | 600 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
5 | Dandenong South | LV | Synchronous - Diesel | Cummins | C1100 D5 | 1100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
6 | Clayton | HV | Synchronous - Diesel | Caterpillar | C175-16 | 13000 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
7 | Glen Waverley | LV | Induction - Hydro | TECO | Francis Hydro Turbine | 560 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
8 | Notting Hill | LV | Induction - Hydro | TECO | Francis Hydro Turbine | 450 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
9 | Rye | HV | Synchronous - Gas | Caterpillar | 3512 | 770 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
10 | Ashburton | LV | Synchronous - Gas | Schmitt Enertec | FMB-285-GSMK | 233 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
11 | Doncaster | LV | Synchronous - Gas | Guascor | SFGLD240 | 550 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
12 | Noble Park | LV | DRUPS | MTU | 16V 4000 G63 | 6200 | 4000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
13 | Dandenong South | LV | Synchronous - Gas | GE Jenbacher | JMC 316 GS | 800 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
14 | Mount Martha | LV | Synchronous - Diesel | Mac Farlane | P1000P1/P1100E1 | 1100 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
15 | Box Hill | HV | Synchronous - Gas | Caterpillar | G3516B | 1450 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
16 | Clayton | LV | Inverter - Microturbine | Capstone Microturbine | C200 C65 | 465 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
17 | Springvale | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 938.4 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
18 | Dandenong South | LV | Inverter - Solar | Fronius | Agilo 100.0-3 | 300 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
19 | Springvale | LV | Inverter - Solar | PowerOne | TRIO-27.6-TL-OUTD | 248.4 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
20 | Boneo | LV | Synchronous Generator | Caterpillar | Engine C32 Frame 1424 | 2250 | 1500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
21 | Moorabbin | LV | Synchronous - Gas | Caterpillar | SR4 Frame 447 Arrangement 1938725 | 237 | 1500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
22 | Chadstone | LV | Synchronous - Gas | R Schmitt Enertec | FMB-320-GSMK | 260 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
23 | Chadstone | LV | Synchronous - Gas | R Schmitt Enertec | FMB-500-GSMK | 400 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
24 | Chadstone | LV | Synchronous - Gas | R Schmitt Enertec | FMB-430-GSMK | 350 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
25 | Frankston | LV | Synchronous - Diesel | Caterpillar | 3512B 512DR7W Arrangement 252-3810 Frame 1447 | 3000 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
26 | Mount Waverley | LV | Induction - Hydro | WEG | 315L/J | 340 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
27 | Dandenong | LV | Induction - Hydro | Siemens | 1LA8353-4EB60-Z | 385 | 500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
28 | Dandenong South | LV | Inverter - Solar | Fronius | 20.0 3M 15.0 3M 8.2 3M | 255 | 500 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
29 | Clayton | HV | DRUPS | Pillar | Uniblock UBTD 2000 | 16000 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
30 | Endeavour Hills | LV | Inverter - Solar | Fronius | Symo 17.5-3-M | 600 | 500 | Type 1 | No | Must be within Distribution Code limits | No | Type 1
31 | Dandenong South | HV | Inverter - Solar | SMA | STP60-10 | 900 | HV Customer | Type 2 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
32 | Mount Waverley | HV | Inverter - Solar DRUPS | Fronius Piller | Symo 20.0-3-M UBR-625 | 645 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
33 | Cheltenham | LV | Inverter - Solar | Fronius | Symo 15.0.3-M Eco 27.0-3-S | 231 | 1000 | Type 2 | Yes | Must be within Distribution Code limits | No | Type 2
34 | Doncaster | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 270 | 500 | Type 2 | Yes | Must be within Distribution Code limits | Yes | Type 3
35 | Dandenong | LV | Synchronous - Diesel | Cummins | C825 D5 | 660 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
36 | Donvale | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 350 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
37 | Lyndhurst | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 324 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
38 | Clayton South | LV | Inverter - Solar | SolarEdge | SE27.6K SE25k | 401 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
39 | Clayton South | HV | Inverter - Solar | SolarEdge | SE27.6K SE25K | 288 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
40 | Carrum Downs | LV | Inverter - Solar | Huawei | SUN2000-33KTL | 240 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
41 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 25.0-3-S SYMO 20.0-3-M SYMO 12.5-3-M | 297.5 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
42 | Brighton | LV | Synchronous - Diesel | Cummins | C300 D5 | 300 | 300 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
43 | Dandenong South | LV | Inverter - Solar | Solis | Solis-30K Solis-15K | 214.5 | 315 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
44 | Pearcedale | LV | Inverter - Solar | Fronius | Fronius Eco 25.0-3-M Fronius Symo 20.0-3-M Fronius Eco 27.0-3-M Fronius Symo 17.5-3-M | 436.5 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
45 | Scoresby | LV | Inverter - Solar | Fronius | ECO 25.0-3-S | 250 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
46 | Braeside | LV | Inverter - Solar | Delta Electronics | RPI M30A | 300 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
47 | Dandenong South | HV | Inverter - Solar | Huawei | SUN2000 33KTL | 1080 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
48 | Boneo | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 1030 | 1000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
49 | Dromana | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
50 | Boneo | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
51 | Rye | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
52 | Dromana | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
53 | Boneo | LV | Synchronous - Diesel | Aggreko G3+ | Stamford PE734C Winding 312 | 2060 | 2000 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
54 | Cheltenham | LV | Synchronous - Diesel | Cummins | C550D5 | 550 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
55 | Keysborough | LV | Inverter - Solar | SMA | STP60000TL | 240 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
56 | Doncaster East | LV | Inverter - Solar | SolarEdge | SE82.8K SE27.6K | 524.4 | 2000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
57 | Glen Waverley | HV | Inverter - Solar | SMA | STP CORE1 50-40 | 250 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
58 | Mulgrave | LV | Inverter - Solar | Fronius | ECO27.0-3-S | 216 | 750 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
59 | Dandenong South | LV | Inverter - Solar | ABB | TRIO-50.0-TL-OUTD | 300 | 750 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
60 | Dandenong South | LV | Inverter - Solar | Solar Edge | SE82.8k | 248.4 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
61 | Dandenong | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 12.5-3-M | 255.5 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
62 | Keysborough | LV | Inverter - Solar | SolarEdge | SE82.8K | 331.2 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
63 | Clayton | LV | Inverter - Solar | Fronius | ECO 27.0-3-S SYMO 17.5-3-M | 845 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
64 | Mitcham | LV | Inverter - Solar | SMA | STP-50-40 | 250 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
65 | Dandenong South | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 270 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
66 | Oakleigh | LV | Inverter - Solar | Solar Edge | SE82.8K | 331.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
67 | Dandenong South | LV | Inverter - Solar | ABB | PVS-100-TL | 1300 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
68 | Oakleigh | LV | Inverter - Solar | Fronius | ECO 27.0-3-S | 513 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
69 | Noble Park | LV | Inverter - Solar | SolarEdge | SE82.8K SE50K | 514 | 1750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
70 | Hawthorn East | HV | Alternator - Diesel | Leroy & Somer | LSA 52.3 S7 – 4P | 3520 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
71 | Frankston | LV | Inverter - Solar | Solar Edge | SE82.8K SE27.6K | 358.8 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
72 | Frankston | LV | Inverter - Solar | Solar Edge | SE82.8K SE27.6K | 634.8 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
73 | Bentleigh East | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S SSE SPS 25 KTL-B | 206 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
74 | Clayton | HV | Inverter - Solar | Solaredge | SE17K SE25K SE27.6K SE50K SE82.8K | 646.4 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
75 | Clayton | LV | Inverter - Solar | Solaredge | SE17K SE50K SE82.8K | 415.2 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
76 | Scoresby | LV | Inverter - Solar | SolarEdge | SE82.8K SE50K SE27.6K | 436.4 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
77 | Braeside | HV | Inverter - Solar | Fronius | ECO 27.0-3-S | 270 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
78 | Burwood East | LV | Inverter - Solar | SMA | STP60-10 | 840 | 3000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
79 | Burwood | LV | Inverter - Solar | Fronius | ECO 27.0-3-S ECO 25.0-3-S SYMO 20.0-3-M SYMO 17.5-3-M SYMO 15.0-3-M SYMO 10.0-3-M | 432.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
80 | Springvale | LV | Inverter - Solar | Fronius | SYMO 15.0-3-M SYMO 20.0-3-M SYMO 25.0-3-S SYMO 27.0-3-S | 214 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
81 | Scoresby | LV | Inverter - Regenerative | AVL | DynoForce ASM 4200/0.65-3 400 T | 928 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
82 | Frankston | LV | Inverter - Solar | Fronius | Eco 27.0-3-S Symo 25.0-3-M | 538 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
83 | Dandenong South | HV | Inverter - Solar | Fronius | ECO 27.0-3-M ECO 25.0-3-S SYMO 15.0-3-M SYMO 10.0-3-M | 1065 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | HV Customer - Site Specific
84 | Dandenong South | LV | Inverter - Solar | ABB | ABB PVS-100 | 300 | 3000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
85 | Rowville | HV | Inverter - Solar | Fronius | ECO27.0-3-S | 864 | HV Customer | Legacy | Legacy | Must be within Distribution Code limits | Legacy | HV Customer - Site Specific
86 | Rosebud | LV | Inverter - Solar | Huawei | SUN2000-50KTL-M0 | 605 | 1000 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
87 | Rosebud | LV | Inverter - Solar | Huawei | SUN2000-50KTL-M0 | 385 | 1500 | Legacy | Legacy | Must be within Distribution Code limits | Legacy | Legacy
88 | Mount Martha | LV | Synchronous - Biogas | 2G Caterpillar | 2G Agenitor 408 CT80 Caterpillar SR4B | 1100 | 500 | Type 4 | Yes | Must be within Distribution Code limits | Yes | Type 4
89 | Rowville | LV | Inverter - Solar | ABB | PVS-100-TL | 600 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
90 | Clayton | HV | Diesel - Synchronous | Caterpillar Cummins | 1 x Stamford 1734G 1 x Stamford SR4B | 9000 | HV Customer | Type 3 | No | Must be within Distribution Code limits | Yes | HV Customer - Site Specific
91 | Burwood | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 25.0-3-S 1 x 27.0-3-S 1 x Symo 10.0-3-M 1 x Symo 15.0-3-M 1 x Symo 17.5-3-M 1 x Symo 20.0-3-M | 492.5 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
92 | Glen Waverley | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 414 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
93 | Glen Waverley | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 331.2 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
94 | Clayton | HV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP20000TL-30 | 900 | HV Customer | Type 3 | No | Must be within Distribution Code limits | No | HV Customer - Site Specific
95 | Dandenong | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP20000TL-30 1 x STP25000TL-30 | 235 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
96 | Boneo | LV | Diesel - Synchronous Natural Gas - Synchronous | 2G Energy AG Caterpillar | 1 x Avus 500 plus BG 1 x C32 1100F | 1788 | 1500 | Type 4 | No | Must be within Distribution Code limits | No | Type 4
97 | Boneo | LV | Diesel - Synchronous Solar - Inverter | Caterpillar Fronius Australia | 1 x 27.0-3-S 1 x C32 1100F | 1127 | 1500 | Type 4 | No | Must be within Distribution Code limits | No | Type 5
98 | Burwood East | LV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP10000TL-20 1 x STP25000TL-30 | 235 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
99 | Boneo | LV | Natural Gas - Synchronous | 2G Energy AG | Avus 500 plus BG | 688 | 2000 | Type 4 | No | Must be within Distribution Code limits | No | Type 4
100 | Mulgrave | LV | Solar - Inverter | Huawei Technologies Co Ltd | 1 x SUN2000-29.9KTL 1 x SUN2000-50KTL-M0 | 224.8 | 3000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
101 | Dandenong South | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 220 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
102 | Clayton | HV | Diesel - Synchronous | Caterpillar | 1250F | 3750 | HV Customer | Type 4 | No | Must be within Distribution Code limits | No | HV Customer - Site Specific
103 | Clayton | LV | Diesel - Synchronous | FG Wilson | 1 x P400E2 1 x P550E1 | 950 | 1000 | Type 4 | No | Must be within Distribution Code limits | No | Type 4
104 | Clayton | HV | Diesel - Synchronous | Leroy Somer | LSA52.3 S6 | 4650 | HV Customer | Type 4 | No | Must be within Distribution Code limits | No | HV Customer - Site Specific
105 | Mulgrave | LV | Solar - Inverter | Fronius Australia Fronius International GmbH | 1 x 27.0-3-S 1 x Symo 20.0-3-M | 425 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
106 | Clayton | HV | Solar - Inverter | SMA Australia Pty Ltd | 1 x STP 50-40 1 x STP10000TL-20 1 x STP25000TL-30 | 360 | HV Customer | Type 4 | No | Must be within Distribution Code limits | No | Type 5
107 | Springvale | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 216 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
108 | Scoresby | LV | Other Energy Source - Inverter Solar - Inverter | AVL SolarEdge Technologies Ltd | 1 x ASM 4200/0.65-3/400T 1 x SE82.8K | 1010.8 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
109 | Dandenong South | LV | Battery - Inverter Diesel - Synchronous Solar - Inverter | Shenzhen Sinexcel Electric Co Ltd SMA Solar Technology AG Staunch | 1 x DC13 072A 1 x PWG2-100K-EX 1 x STP 110-60 | 953 | 1500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
110 | Mulgrave | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 243 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
111 | Frankston | LV | Solar - Inverter | Fronius Australia | 27.0-3-S | 459 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
112 | Moorabbin | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 496.8 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
113 | Somerville | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE82.8K | 414 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
114 | Somerville | LV | Solar - Inverter | SolarEdge Technologies Ltd | 1 x SE50K 1 x SE82.8K | 298.4 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
115 | Moorabbin Airport | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
116 | Moorabbin Airport | LV | Solar - Inverter | SMA Australia Pty Ltd | STP110-60 | 550 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
117 | Keysborough | LV | Solar - Inverter | Huawei Technologies Co Ltd | SUN2000-50KTL-M0 | 275 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
118 | Chadstone | LV | Solar - Inverter Solar and Battery - Inverter | Fronius Australia Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x SG50CX 1 x Symo 20.0-3-M 1 x Symo GEN24 10.0 Plus | 249.7 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
119 | Moorabbin | LV | Diesel - Synchronous Solar - Inverter | Caterpillar Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x 1938725 447 1 x SG110CX 1 x SG30CX 1 x Symo 5.0-3-M | 611.9 | 1500 | Type 4 | No | Must be within Distribution Code limits | No | Type 5
120 | Chadstone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 320 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
121 | Chadstone | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
122 | Chadstone | LV | Solar - Inverter | Fronius International GmbH Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX 1 x Symo 10.0-3-M | 490 | 6000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
123 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
124 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 880 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
125 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 880 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
126 | Braeside | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 440 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
127 | Rowville | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
128 | Scoresby | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 440 | 500 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
129 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 469.9 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
130 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 2000 | Type 3 | No | Must be within Distribution Code limits | No | Type 2
131 | Dandenong South | LV | Battery - Inverter Solar - Inverter | Delta SolarEdge Technologies Ltd | 1 x PCS100HV 1 x SE82.8K | 2242 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
132 | Burwood | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 260 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
133 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
134 | Keysborough | LV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 | 330 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
135 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
136 | Frankston | LV | Natural Gas - Microturbine Solar - Inverter | Capstone Sungrow Power Supply Co Ltd | 1 x C65 ICHP-DM 1 x SG110CX | 570 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
137 | Chelsea | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
138 | Clayton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
139 | Moorabbin | LV | Solar - Inverter | Fronius Australia | 1 x 25.0-3-S 1 x 27.0-3-S | 208 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
140 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
141 | Mulgrave | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
142 | Mulgrave | LV | Solar - Inverter | SMA Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX 1 x STP25000TL-30 | 295 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
143 | Dromana | LV | Battery - Inverter | Delta Electronics Inc | PCS100HV | 1000 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
144 | Dandening South | LV | Battery - Inverter Diesel - Synchronous Solar - Inverter | Staunch Sungrow Power Supply Co Ltd | 1 x SC50HV 1 x SG110CX 1 x STSG456 | 886 | 1500 | Type 3 | No | Must be within Distribution Code limits | Yes | Type 2
145 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 4000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
146 | Moorabbin | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
147 | Mulgrave | LV | Solar - Inverter | SolarEdge Technologies Ltd Sungrow Power Supply Co Ltd | 1 x SE5K 1 x SG110CX | 225 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
148 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
149 | Mulgrave | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW80K-MT | 240 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
150 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
151 | Glen Waverley | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
152 | Mornington | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
153 | Langwarrin | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 660 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
154 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
155 | Dandenong South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro 50-3-D | 500 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
156 | Malvern East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG30CX | 359.9 | 6500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
157 | Carrum Downs | LV | Solar - Inverter | SolarEdge Technologies Ltd | SE30K | 300 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
158 | Mentone | HV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG20RT | 240 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
159 | Burwood East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 270 | 2500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
160 | DANDENONG SOUTH | LV | Solar - Inverter | Fronius | Tauro 100-3-D | 300 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
161 | Mulgrave | LV | Solar - Inverter | Jiangsu GoodWe Power Supply Technology Co Ltd | GW80K-MT | 299 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
162 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 550 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
163 | Bentleigh East | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 300 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
164 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 330 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
165 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
166 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX | 270 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
167 | Rowville | HV | Battery - Inverter | BYD | 1 x BEM320KTL-E-R1 1 x BEM480KTL-E-R1 | 500 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
168 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
169 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
170 | Mentone | LV | Solar - Inverter | Fronius Australia Pty Ltd Fronius International GmbH | 1 x Symo 15.0-3-M 1 x Symo 20.0-3-M 1 x Tauro Eco 100-3-D | 350 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
171 | Mentone | LV | Solar - Inverter | Fronius Australia Fronius Australia Pty Ltd Fronius International GmbH | 1 x 25.0-3-S 1 x Symo 15.0-3-M 1 x Tauro 50-3-D 1 x Tauro Eco 100-3-D | 215 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
172 | Clayton | HV | Solar - Inverter | SMA Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SG110CX 1 x SG50CX 1 x STP10000TL-20 | 1280 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
173 | Wantirna South | LV | Solar - Inverter | SMA Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SG30CX 1 x STP 110-60 | 440 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
174 | DANDENONG SOUTH | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) | 270 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
175 | Clayton South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 220 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
176 | Clayton | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 2 x SG110CX (AS4777-2 2020) | 220 | 500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
177 | WHEELERS HILL | LV | Solar - Inverter | Fimer SpA Sungrow Power Supply Co Ltd | 1 x PVS-20-TL-SX (AS4777-2 2020) 1 x SG110CX (AS4777-2 2020) 1 x SG30CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) | 380 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
178 | MOUNT WAVERLEY | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) | 380 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
179 | Clayton | HV | Solar - Inverter | SMA Australia Pty Ltd | STP 110-60 (AS4777-2 2020) | 550 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 2
180 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 440 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
181 | Moorabbin | LV | Solar - Inverter | Fronius Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SG110CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) 1 x Symo 20.0-3-M (AS4777-2 2020) | 240 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
182 | Carrum Downs | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 660 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
183 | Dandenong | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | 1 x SG110CX (AS4777-2 2020) 1 x SG50CX (AS4777-2 2020) | 380 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
184 | CARRUM DOWNS | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 330 | 1500 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
185 | Scoresby VIC | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 330 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
186 | Clayton South | LV | Solar - Inverter | Fronius Australia Pty Ltd | Tauro Eco 100-3-D (AS4777-2 2020) | 500 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | Yes | Type 3
187 | Rowville | LV | Solar - Inverter | Fronius Australia Pty Ltd Sungrow Power Supply Co Ltd | 1 x SG110CX (AS4777-2 2020) 1 x Symo 20.0-3-M (AS4777-2 2020) | 630 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
188 | Mulgrave | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 330 | 750 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
189 | Nunawading | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 220 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
190 | Mulgrave | LV | Solar - Inverter | GoodWe Technologies Co Ltd | GW80K-MT (AS4777-2 2020) | 240 | 1000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
191 | Dandenong South | LV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 440 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
192 | Notting Hill | LV | Battery - Inverter | Sungrow Power Supply Co Ltd | ST570kWh-250kW-2h-AU | 750 | 2000 | Type 3 | Yes | Must be within Distribution Code limits | No | Type 2
193 | Dandenong South | HV | Solar - Inverter | Sungrow Power Supply Co Ltd | SG110CX (AS4777-2 2020) | 440 | HV Customer | Type 3 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific
194 | Frankston | LV | Diesel - Synchronous | Caterpillar | 3516C | 7500 | 4000 | Type 4 | No | Must be within Distribution Code limits | No | Type 2
195 | Hastings | HV | Gas - Synchronous | Solar Turbine | T130 | 43000 | HV Customer | Type 4 | Yes | Must be within Distribution Code limits | No | HV Customer - Site Specific

## Prot Types
Protection Type | Generator Protection Functions | Central/Secondary Prot Relay Functions | Comments
1 | Over Frequency | No Secondary Protection Relay | Applicable to inverter based installations with total capacity < 100kVA whose application was submitted prior to 1 May 2017
Under Frequency
Over Voltage
Under Voltage
2 | Over Frequency | Over Frequency | Applicable to inverter based installations with total capacity > 100kVA whose application was submitted prior to 1 May 2017
| Under Frequency | Under Frequency
| Over Voltage | Over Voltage
| Under Voltage | Under Voltage
ROCOF
Vector Shift
3 | Over Frequency | Over Frequency | Applicable to all negotiated inverter based installations whose application was submitted after or on 1 May 2017
| Under Frequency | Under Frequency
| Fast Over Voltage | Fast Over Voltage
| Over Voltage | Over Voltage
| Sustained Over Voltage | Sustained Over Voltage
| Under Voltage | Under Voltage
| Soft Export Limit (where applicable) | ROCOF
Vector Shift
Reverse Power (where applicable)
4 | Over Frequency | Over Frequency | Applicable to all non-inverter based installations
| Under Frequency | Under Frequency
| Fast Over Voltage | Fast Over Voltage
| Over Voltage | Over Voltage
| Under Voltage | Under Voltage
| ROCOF | ROCOF
| Vector Shift | Vector Shift
| Reverse Power | Reverse Power (where applicable)
| Synch Check | Synch Check
Current based protection (O/C, E/F)
Negative Sequence Protection
Neutral Voltage Displacement (where possible) - e.g. HV customer not connected to a REFCL enabled feeder